© ISO New England Inc.

November 6, 2014

2014 Regional System Plan

Preface

ISO New England Inc. (ISO) is the not-for-profit corporation responsible for the reliable and economical operation of New England’s electric power system. It also administers the region’s wholesale electricity markets and manages the comprehensive planning of the regional power system. The planning process includes the preparation of an annual Regional System Plan (RSP) in accordance with the ISO’s Open Access Transmission Tariff (OATT) and other parts of the Transmission, Markets, and Services Tariff (ISO tariff), approved by the Federal Energy Regulatory Commission (FERC). Regional System Plans meet the tariff requirements by including the following:

- Forecasts of annual energy use and peak loads (i.e., the demand for electricity) for a 10-year planning horizon and the need for resources (i.e., capacity)

- Information about the amounts, locations, and characteristics of market responses (e.g., generation or demand resources or elective transmission upgrades) that can meet the defined system needs—systemwide and in specific areas

- Descriptions of transmission projects for the region that could meet the identified needs, as summarized in an RSP Project List, which includes information on project status and cost estimates and is updated several times each year.

RSPs also must summarize the ISO’s coordination of its short- and long-term system plans with those of neighboring systems, the results of economic studies of the New England power system, and information that can be used for improving the design of the regional wholesale electricity markets. In addition to these requirements, the RSPs identify the initiatives and other actions taken by the ISO, state officials, regional policymakers, participating transmission owners (PTOs), New England Power Pool (NEPOOL) members, market participants, and other stakeholders to meet or modify the needs of the system.

The 2014 Regional System Plan (RSP14) and the regional system planning process identifies the region’s electricity needs and plans for meeting these needs for 2014 through 2023.

Regional Power System Evolution and System Planning Achievements

New England’s transmission owners have placed in service transmission projects throughout the region to provide solutions to the needs identified through the regional planning process, as detailed in past RSPs and supporting reports. These projects have reinforced the transmission facilities serving the entire region with upgrades in all six New England states. The projects also have reinforced the system in critical “load pockets,” such as Southwest Connecticut (SWCT) and Boston, allowing the import of power from other parts of the system. New interconnections with neighboring power systems also have been placed in service, strengthening the region’s ability to interchange power with these systems. From 2002 to June 2014, 559 projects were put into service, totaling approximately $6.6 billion of new infrastructure investment.

In addition to transmission development, market participants and the states have responded to the need for electric energy and capacity resources. From November 1997 through April 2014, new generating projects totaling 14,995 megawatts (MW) have interconnected to the New England power system, and 4,114 MW of primarily older, less efficient resources have retired from the system. Active and passive demand resources, currently totaling 2,100 MW, are part of the regional power system, and 2,950 MW are expected by 2017. New England states’ annual investments in energy-efficiency (EE) programs are expected to exceed $900 million per year for 2018 through 2023. These EE investments remain a large part of the expansion in passive demand resources, which are projected to grow at approximately 200 MW per year across the 10-year horizon.

RSP14 Review and Approval

The regional system planning process in New England is open and transparent and reflects advisory input from regional stakeholders, particularly members of the Planning Advisory Committee (PAC), according to the requirements specified in the OATT. The PAC is open to all entities interested in regional system planning activities in New England.

The ISO and the PAC have discussed study proposals, scopes of work, assumptions, draft and final study results, and other materials appearing in RSP14. From September 2013 through August 2014, the ISO hosted 15 PAC meetings, and 197 stakeholder representatives from 109 entities attended at least one meeting. The ISO also posted to its website PAC presentations, meeting minutes, reports, databases, and other materials. In addition, the ISO held a public meeting on September 11, 2014, to discuss RSP14 and other planning issues facing the New England region.

As required by the OATT Attachment K, the ISO New England Board of Directors has approved the 2014 Regional System Plan.

Contents

Preface	i

Figures	vii

Tables	ix

Section 1
Executive Summary	1

1.1 Overview of the 2014 Regional System Plan	2

1.2 Overview of System and Strategic Planning Issues	4

1.3 Major Findings and Observations	8

1.3.1 Forecasts of Peak Demand, Annual Use of Electric Energy, Effects of Energy-Efficiency Measures,
and Distributed Generation	8

1.3.2 Needs for Capacity and Operating Reserves	11

1.3.3 Transmission System Needs and Solutions	13

1.3.4 Regional Strategic Planning	16

1.3.5 Interregional Planning	22

1.3.6 State, Regional, and Federal Initiatives that Affect System Planning	23

1.4 Conclusions	24

Section 2
Introduction	25

2.1 Overview of the System Planning Process and RSP14	25

2.1.1 Planning Studies Conducted for and Summarized in RSP14	27

2.1.2 Other Planning Considerations	28

2.2 Overview of the New England Electric Power System	31

2.3 Overview of the New England Wholesale Electricity Market Structure	32

2.4 Overview of System Subdivisions Used for Analyzing and Planning the System	33

Section 3
Forecasts of New England’s Peak Demand, Annual Use of Electric Energy, Energy Efficiency,
and Distributed Generation	37

3.1 ISO New England Load Forecasts	37

3.1.1 Economic and Demographic Factors and Electric Energy Use	39

3.1.2 The CELT Forecast and Passive Demand Resources	41

3.1.3 Subarea Use of Electric Energy	42

3.2 Energy-Efficiency Forecast for New England	45

3.3 Load Forecast Incorporating Results for FCA #8 and the 2014 Energy-Efficiency Forecast	46

3.4 Distributed Generation Forecast	48

3.4.1 Background	48

3.4.2 Development of a PV Forecast Methodology	49

3.4.3 Data Collection	49

3.4.4 PV Forecast	50

3.4.5 Next Steps	52

3.5 Summary of Key Findings of the Load, Energy-Efficiency, and PV Forecasts	53

Section 4
Resources—Adequacy, Capacity, and Reserves	54

4.1 Determining Systemwide and Local-Area Capacity Needs	54

4.1.1 Systemwide Installed Capacity Requirements	55

4.1.2 Local Resource Requirements and Limits	56

4.1.3 Capacity Supply Obligations from the Forward Capacity Auctions	57

4.2 FCM Capacity Zones	62

4.3 Determining Operating Reserves and Regulation	65

4.3.1 Systemwide Operating-Reserve Requirements	66

4.3.2 Locational Forward Reserve Market Requirements for Major Import Areas	67

4.4 Analyzing Operable Capacity	70

4.5 Identifying New England’s Generating Resources	72

4.5.1 Existing Generating Resources in New England	73

4.5.2 Generating Units in the ISO Generator Interconnection Queue	75

4.6 Summary	77

Section 5
Transmission Security and Upgrades	79

5.1 The Need for Transmission Security	81

5.2 Types of Transmission Upgrades	81

5.2.1 Reliability Transmission Upgrades	81

5.2.2 Market Efficiency Transmission Upgrades	82

5.2.3 Generator Interconnection Upgrades and Generator Interconnection-Related Upgrades	83

5.2.4 Elective Transmission Upgrades and Merchant Transmission Facilities	83

5.3 RSP Project List and Projected Transmission Project Costs	83

5.4 Transmission System Performance Needs Assessments and Upgrade Approvals	87

5.4.1 Northern New England	89

5.4.2 Southern New England	98

5.5 Information on Critical Load Levels	116

5.6 Transmission Improvements to Load and Generation Pockets Addressing Reliability Issues	117

5.7 Delist Bids, FCA #4 to FCA #8	118

5.8 Other Needed and Elective Transmission Upgrades	119

5.8.1 Needed Market-Efficiency-Related Transmission Upgrades	119

5.8.2 Transmission Improvements to Mitigate Congestion	120

5.8.3 Reliability Transmission Upgrade Improvements to Load and Generation Pockets	120

5.8.4 Required Generator-Interconnection-Related Upgrades	121

5.8.5 Elective Transmission Upgrades	121

5.9 Summary	122

Section 6
Studies and Other Actions Supporting the Strategic Planning of the Region	124

6.1 Capacity and Electric Energy Production in the Region by Fuel Type	124

6.2 Natural Gas and Oil Fuel-Certainty Issues for Power Generation	126

6.2.1 Natural Gas Infrastructure—Issues and Improvements	127

6.2.2 Overview of Winter 2013/2014 Operations	131

6.2.3 Studies on Natural Gas Supply and Delivery to Power Generators	140

6.2.4 Addressing Regional Fuel-Certainty Issues	142

6.3 Impacts of Environmental Regulations on Generators and the Power System Overall	147

6.3.1 Emerging Impacts of Clean Water Act Regulations on the Region’s Generators	148

6.3.2 Clean Air Act Requirements and Regional and Federal Greenhouse Gas Regulations	150

6.3.3 Cost of Compliance with Environmental Regulations	155

6.4 Update of Regional Nuclear Generation Licensing Renewals	155

6.5 Update on Hydroelectric Generation Relicensing	156

6.6 Wind and Photovoltaic Integration Activities	157

6.6.1 Potential System Impacts on Fossil Fuel Generators of Integrating Wind and Solar Resources	157

6.6.2 Wind Forecasting and Dispatch	157

6.6.3 Strategic Transmission Analyses—Wind Integration Study	158

6.7 Large-Scale Adoption of Photovoltaic Resources and Other Distributed Generation Resources	160

6.7.1 Operational Solar Forecasting	160

6.7.2 PV and Long-Term Planning	161

6.7.3 Potential Reliability Impacts of PV	161

6.8 Economic Performance of the System and Other Studies	162

6.8.1 Economic Studies	163

6.8.2 Generic Capital Costs of New Supply Resources	165

6.9 Strategic Transmission Analyses—Generator Retirement Analysis	166

6.10 Analysis of Market-Resource Alternatives (MRAs) in Load Pockets	167

6.11 Summary	168

Section 7
Planning Coordination, Studies, and Initiatives	170

7.1 Interregional Coordination and Initiatives	170

7.1.1 Eastern Interconnection Planning Collaborative Studies of the Eastern Interconnection	170

7.1.2 Electric Reliability Organization Overview	171

7.1.3 IRC Activities	172

7.1.4 Northeast Power Coordinating Council Studies and Activities	172

7.1.5 Northeastern ISO/RTO Planning Coordination Protocol	173

7.1.6 Interregional Transfers	174

7.2 Federal Initiatives	175

7.2.1 FERC Order No. 1000	175

7.2.2 US Department of Energy Congestion Studies	175

7.2.3 Quadrennial Energy Review	176

7.2.4 Executive Orders on Cybersecurity	177

7.2.5 FERC Directive on Physical Security	177

7.3 Regional Initiatives	177

7.3.1 Coordination among the New England States	177

7.3.2 Consumer Liaison Group	178

7.4 ISO Initiatives	179

7.4.1 Improving the Wholesale Electricity Markets	179

7.4.2 Updates on Developing and Integrating Smart Grid and Other New Technologies	179

7.4.3 Draft Transmission Planning Process Guide and Draft Transmission Planning Technical Guide	182

7.5 State Initiatives, Activities, and Policies	183

7.5.1 Connecticut	183

7.5.2 Maine	184

7.5.3 Massachusetts	185

7.5.4 New Hampshire	186

7.5.5 Rhode Island	188

7.5.6 Vermont	189

7.5.7 Summary of Renewable Portfolio Standards	189

7.6 Summary of Initiatives	189

Section 8
Key Findings and Conclusions	191

8.1 Forecasts of Peak Load, Energy Use, and Energy Efficiency	191

8.2 Distributed Generation Forecast	191

8.3 Systemwide and Local Area Needs for Capacity	191

8.4 Operating Reserves and Ancillary Services	192

8.5 Transmission Projects	192

8.6 Market Resource Alternatives to Transmission	193

8.7 Fuel Flexibility and Certainty	194

8.8 State Targets for Renewable Energy	194

8.9 Integration of Intermittent Resources	195

8.10 Environmental Regulations and Initiatives	195

8.11 Interregional Coordination	196

8.12 Federal, Regional, and State Initiatives	196

8.13 Looking Ahead	196

Appendix A
Acronyms and Abbreviations	197

# Figures

Figure 2-1: 	Key facts about New England’s electric power system and wholesale electricity markets.	31

Figure 2-2: 	Active-demand-resource dispatch zones in the ISO New England system.	35

Figure 2-3: 	RSP14 geographic scope of the New England electric power system.	36

Figure 3-1: 	The ISO’s actual summer peak loads (i.e., reconstituted for OP 4 and FCM passive demand resources) and the 50/50 and 90/10 forecasts, 1992 to 2013 (MW).	39

Figure 3-2: 	“Economy.com” forecasts of New England gross state product from November 2013
and November 2012 forecasts.	41

Figure 3-3:	RSP14 annual energy-use forecast (diamond), energy-use forecast minus FCM #8 results
through 2017 (square), and energy-use forecast minus FCM results and minus the
energy-efficiency forecast (triangle) for 2018 to 2023 (GWh).	47

Figure 3-4:	RSP14 summer peak demand forecast (90/10) (diamond), demand forecast minus FCM #8
results through 2017 (square), and demand forecast minus FCM results and minus the energy-efficiency forecast (triangle) for 2018 to 2023 (MW).	47

Figure 4-1: 	Projected summer operable capacity analysis, 2014 to 2023.	71

Figure 4-2: 	Capacity of generation-interconnection requests by RSP subarea, November 1997
to April 2014.	75

Figure 4-3: 	Resources in the ISO Generator Interconnection Queue, by state and fuel type
 as of April 1, 2014 (MW and %).	76

Figure 4-4: 	Resources in the ISO Generator Interconnection Queue, by RSP subarea and fuel type,
as of April 1, 2014 (MW).	77

Figure 4-5: 	Percentage of resources in the ISO Generator Interconnection Queue, by RSP subarea
and fuel type, as of April 1, 2014.	77

Figure 5-1: 	Approximate geographic region of each of the 14 major transmission projects in New England,
as of June 1, 2014.	80

Figure 5-2: 	Map of constraints in southern New England.	101

Figure 6-1: 	New England’s summer seasonal claimed capability and electric energy production
by fuel type for 2013.	125

Figure 6-2: 	Generating resource summer capability by fuel type based on the 2014 CELT Report
and the interconnection queue (MW, %).	126

Figure 6-3:	Overview map of the natural gas infrastructure serving New England.	128

Figure 6-4: 	LNG sendout from Canaport LNG terminal/Maritime pipeline and Everett LNG terminal,
November 2010 to May 2013 (MMcf/d).	129

Figure 6-5: 	Northeast natural gas pipeline constraints (left) and recent pipeline-capacity additions,
2011 (right).	130

Figure 6-6: 	Generator energy production by fuel type for December 2013, and January, February,
and March 2014.	133

Figure 6-7: 	Depletion of oil storage inventories at regional generation facilities.	133

Figure 6-8: 	Hourly real-time locational marginal prices, December 1 to 31, 2013.	135

Figure 6-9: 	Generation by fuel type compared with CSOs, January 7, 2014, evening peak (MW).	137

Figure 6-10: 	Generation by fuel type, January 7, 2014, evening peak (%)	137

Figure 6-11: 	Real-time energy prices compared with regional natural gas prices ($/MWh; $/MMbtu).	139

Figure 6-12: 	Daily day-ahead and real-time ISO New England Hub prices and input fuel prices,
January 1 to 31, 2014 ($/MWh; $/MMBtu).	139

Figure 6-13: 	Number of cooling systems in the United States by primary energy source, 2012.	148

Figure 6-14: 	Annual average NOX, SO2 and CO2 emission rates, 2001 to 2012 (lb/MWh).	152

Figure 6-15: 	RGGI CO2 emissions cap compared with actual/projected emissions (2005 to 2020).	153

Figure 6-16: 	Areas (in blue), in Connecticut (left) and Massachusetts (right), where PV resources
are likely to trip off line because of low voltage in the event of a fault on the 345 kV
transmission system.	162

Figure 7-1: 	2013 energy imports and exports by external area (GWh).	174

Figure 7-2: 	Existing and planned FACTS devices in New England.	181

Figure 7-3: 	Large-scale transmission in New England, including some proposed direct-current
transmission.	182

# Tables

Table 3-1 	Summary of Annual Electric Energy Use and Peak Demand Forecast for New England
and the States, 2014/2015 and 2023/2024	38

Table 3-2 	New England Economic and Demographic Forecast Summary	40

Table 3-3 	Forecasts of Annual Use of Electric Energy and Peak Demand in RSP Subareas, 2014 and 2023	43

Table 3-4	Forecasts of RSP Subarea Peak Demand, 2014	44

Table 3-5	ISO New England’s Final Energy-Efficiency Forecast for 2018 to 2023 (GWh, MW)	46

Table 3-6 	2014 Forecasts of Annual and Peak Electric Energy Use Compared with the Forecast Minus
FCM Passive Demand Resources (2014 to 2017) and Energy-Efficiency Forecast Results
(2018 to 2023)	48

Table 3-7 	Discount Factor Percentages for New England State Policy-Supported Megawatts of PV,
2013 to 2023 and Post-Policy Years	50

Table 3-8 	State-by-State Annual and Cumulative PV Nameplate Capacity Forecast after Applying
Discount Factors, 2013 to 2023 (MWAC)	51

Table 4-1	Actual and Representative New England Net Installed Capacity Requirements and Resulting Reserves, 2014 to 2023 (MW, %)	56

Table 4-2 	Actual LSRs and MCLs for the 2014/2015 to 2017/2018 Capacity Commitment Periods	57

Table 4-3 	Summary of the FCA Obligations at the Conclusion of Each Auction (MW)	58

Table 4-4 	Results of the FCA by Capacity Zone at the Conclusion of Each Auction (MW, $/kW-month)	59

Table 4-5 	Capacity Supply Obligation for New Capacity Procured during the Forward Capacity
Auctions (MW)	61

Table 4-6	Future Systemwide Needs (MW)	62

Table 4-7 	Results of the Transfer Capability Analysis for New England, 2014 to 2023 (MW)	64

Table 4-8 	Representative Future Operating-Reserve Requirements in Major New England Import
Areas (MW)	68

Table 4-9 	Projected New England Operable Capacity Analysis for Summer, 2014 to 2023,
Assuming 50/50 Loads (MW)	71

Table 4-10 	Projected New England Operable Capacity Analysis for Summer, 2014 to 2023,
Assuming 90/10 Loads (MW)	72

Table 4-11	2014 Summer Seasonal Claimed Capability for ISO New England Generating Resources,
by Assumed Operating Classification, Systemwide, and by RSP Subarea (MW)	73

Table 4-12 	RSP14 Generating Capacity by Subarea, Load Zone, and State, 2014	74

Table 4-13 	Summary of Queue Projects as of April 1, 2014	76

Table 5-1 	Estimated Cost of Reliability Projects as of June 2014 Plan Update (Million $)	85

Table 5-2 	Actual and Forecast Regional Network Service Rates, 2012 to 2017	87

Table 5-3 	Net Commitment-Period Compensation by Type and Year (Million $)	120

Table 6-1 	New England Operating Nuclear Power Plants	156

Table 6-2	Generic Capital Costs of New Supply-Side Resources	166

# Executive Summary

ISO New England’s (ISO) regional system planning process and market design have fostered significant additions to the region’s generation and demand resources. Approximately 10% of the region’s existing generation was built during the past 10 years, and the amount of energy efficiency participating as demand resources in the Forward Capacity Market (FCM) has increased roughly 235 megawatts (MW) per year over the past four years. The transmission system, which had seen little investment in past decades, has been upgraded over the past 10 years to reduce congestion and better serve the region’s load.

To maintain the reliable and efficient operation of the New England power system, the regional system planning process is continuous and comprehensive. But notwithstanding the region’s system improvements, challenges remain across the 10-year planning horizon for maintaining system reliability, including the following:

- Improving resource performance and flexibility

- Maintaining reliability and fuel certainty, given the region’s increased reliance on natural-gas-fired capacity and the limited availability of fuels necessary to generate electrical energy

- Planning for the potential retirement of generators

- Integrating a greater level of intermittent resources (i.e., variable energy resources; VERs)

To address these regional strategic planning issues, prepare for changes likely to confront the New England power system, and assess potential system enhancements, the ISO and its stakeholders are modifying the market design, system operations, and planning activities. These planning activities, which are designed to ensure a reliable and economical power system, take place through an open stakeholder process that includes input from the Planning Advisory Committee (PAC). Additionally, the ISO receives advisory input through the New England Power Pool (NEPOOL) committee structure on potential changes to the market design, provisions of the Open Access Transmission Tariff (OATT), and supporting procedures.

Historically, the region has supported the reliable operation of the system through proactive planning, the completion of transmission projects and other improvements, the development of needed resources, and the overall competitiveness of the markets. The ISO anticipates that compliance with the Federal Energy Regulatory Commission’s (FERC) final Order No. 1000 will require fundamental changes to the transmission planning process as it has been conducted in New England since 2001. Opening the process to nonincumbent transmission developers and implementing a competitive solicitation process for transmission solutions are key components of this order. The order also requires the planning process to address public policy objectives and includes modifying the interregional planning processes, as well. The final scope and substance of the changes to the regional system planning process are still uncertain pending the final FERC order and court decisions.

The ISO is conducting its ongoing regional planning activities under the following set of system considerations:

- Low net load growth due to a slow recovery from the recession and the forecast of energy-efficiency resources

- Existing level, types, and locations of resources, the development of new resources, and the retirement of others

- $4.5 billion additional transmission improvements planned for the region, consistent with federal and regional reliability standards

- The results from interregional coordination and planning studies the ISO performs with neighboring regions

The regional planning process has been robust and able to foster the development of required infrastructure through the ISO’s partnership with the states, market participants, transmission owners, and other stakeholders. The ISO is committed to procuring adequate resources and remains hopeful that the region will install the required types of demand and supply resources where and when needed. Transmission projects have been placed in service successfully, and others are under development. The ISO will continue to work through the PAC and NEPOOL processes to meet and implement all requirements as they continue to evolve.

This Executive Summary provides an overview of the 2014 Regional System Plan, a summary of the results of system and strategic planning studies, and the highlights of key findings and observations. The main sections of RSP14 summarize major assumptions, study results, and issues and include references to reports and presentations that provide detailed information to interested readers. Italicized terms throughout the report indicate that a definition for the term is included within the text or footnotes; links to other documents that more fully define the more complex terms are provided. Appendix A is a list of acronyms and abbreviations used in RSP14.

## Overview of the 2014 Regional System Plan

The 2014 Regional System Plan (RSP14) builds on the results of previous regional system plans and analyses. It provides information on electric power system needs; system improvements; and the results of newly completed load, resource, and transmission studies for reliably meeting demand throughout the region to 2023. It also discusses ongoing and new analyses based on the current and planned system and describes new and planned infrastructure for all areas of New England. The report also addresses many of the challenges the region is facing and how the ISO and its stakeholders are addressing key strategic issues. Notably, the report addresses the major factors influencing resource development, the requirements for fuel certainty, and the development of the electric power system infrastructure for the 10-year planning period, such as existing and pending state and federal environmental and energy policies.

RSP14 and the ongoing system planning process comply with all applicable sections of the ISO’s Transmission, Markets, and Services Tariff (ISO tariff), approved by FERC. The plan and planning process also satisfy the relevant standards, criteria, and other requirements established by the North American Electric Reliability Corporation (NERC), the Northeast Power Coordinating Council (NPCC), participating transmission owners (PTOs), and the ISO. As part of its compliance with Attachment K of the ISO’s Open Access Transmission Tariff (OATT), RSP14 specifically provides information on the timing of system needs and the quantity, general locations, and characteristics of the generation and demand resources that could resolve these needs and defer or eliminate the need for transmission projects. The results of various system and regional strategic planning studies and other materials, as follows, provide this information:

- Forecasts of the average electric energy usage annually and at the peak hour for 2014 to 2023—for the entire system, individual states, and smaller areas of the power system (see Section 3.1)

- Planned long-term energy efficiency (EE) additions for 2014 through 2017 and forecasts of the EE savings in the six New England states, annually and at the peak hour for 2018 to 2023 (see Section 3.2)

- Forecasts of the growth of photovoltaic (PV) resources in the region from 2014 through 2023 (see Section 3.4)

- Projections of the systemwide need for both capacity and operating reserves and the identification and evaluation of the locations where fast-start resources (i.e., those available for service within 10 minutes or within 30 minutes) would be the most beneficial (Sections 4.1 and 4.3)

- Evaluations of interface transfer capabilities relevant to capacity zone modeling, which when combined with other RSP14 information, help market participants identify the portions of the system with potential resource surpluses or shortfalls (see Section 4.2)

- Analyses and operating experience that show the vulnerabilities associated with the regional reliance on natural gas and the benefits of having more reliable access to gas supplies, dual-fuel capabilities, and other fuel sources (see Section 6.22)

- Existing and pending environmental regulations, emissions analyses, and economic studies, which show the effects of using efficient, low-emitting resources; greater amounts of renewable resources; and increased energy efficiency on regional air emissions and the economic performance of the system (see Section 6.3)

- Economic studies of resource retirements and expansion, which describe the effects of varying amounts, locations, and types of resources and imports from neighboring systems on system performance (see Section 6.8)

- The Strategic Transmission Analysis, which provides insight on beneficial electrical locations for resource development and the effects of extensive generation retirements across the region (Section 6.9)

- Planning analyses of wind and photovoltaic resources, the status of revisions to the interconnection requirements, tools for developing forecasts, and the identification of systemwide needs for successfully integrating and operating variable resources on a large-scale (see Section 6.6)

- Studies of market resource alternatives (MRAs) in the Southeast Massachusetts/Rhode Island load pockets (see Section 6.10)

- Summaries of regional and interregional transmission planning studies (i.e., needs assessments and solutions studies), which provide detailed information to resource developers and other stakeholders on potential infrastructure additions (Section 5)

## Overview of System and Strategic Planning Issues

The New England system requires resources that provide flexible capacity and energy supply and transmission to carry electric energy where needed. Improvements in the markets, the development of new resources, and transmission upgrades are helping meet these regional needs. Interregional planning studies, especially for ensuring reliable infrastructure development, have become increasingly important, and the ISO is coordinating planning efforts in the Northeast and throughout the Eastern Interconnection. Regional initiatives on improving the wholesale electricity markets, applying advanced technologies, and developing regional policies and procedures are affecting the evolution of the New England electric power system.

Similar to the RSP13 forecast, the RSP14 regional forecast shows slow growth in both the summer and winter peak demand of 1.3% and 0.6%, respectively, and annual energy use of 1%. The energy-efficiency forecast also is similar to the RSP13 forecast and shows a further slowing of net load growth to about half the growth rate of the summer peak load and essentially no net growth in both the winter peak load and regional annual use of energy. The ISO issued a multistate forecast of photovoltaic resources and is working with stakeholders to expand the forecast to cover all distributed generation (DG) resources.

Despite the slow growth in demand, RSP14 shows that the region requires additional reliable capacity, which can be achieved by developing new resources and improving the performance of existing resources. Over 4,000 MW of resource retirements are expected from June 2014 through June 2017, stemming from nonprice retirement requests by demand and supply resources, and additional generators are likely to retire as a result of their not being economically competitive. Few new resources cleared the eighth Forward Capacity Auction (FCA #8), and the region is projected to require new resources from 2017 through 2023. To ensure resource adequacy in the region, the ISO expects to procure needed resources through the Forward Capacity Market. Additional market performance incentives are aimed at further encouraging resource owners to improve their performance and develop capacity, including demand resources and new resources listed in the ISO New England Generator Interconnection Queue (the queue). Some of the key market improvements to the day-ahead and real-time markets, as well as changes to the FCM, are as follows:

- “Pay for performance,” designed to encourage the operation of resources when most needed, including during scarcity events, by creating stronger financial incentives to produce electric energy and to supply reserves (to be implemented on June 1, 2018)

- A sloped demand curve for capacity auctions, designed to reduce the volatility in capacity prices between periods of excess supply and periods when new capacity resources are needed, which may occur as aging plants retire (to be implemented for the FCA #9 primary auction and for the associated reconfiguration auctions)

- An update of the methodology for identifying and forming capacity zones to be used in the FCAs that reflect changing system conditions and encourage the development of capacity resources in needed locations (to be reflected in FCA #9, reconfiguration auctions, and settlements)

To further support the region’s need for reliable capacity and because New England has become an energy-constrained system in recent years, New England requires fuel certainty. The need for greater fuel certainty to maintain reliability was evident in 2013 and 2014, when the region’s heavy dependence on natural-gas-fired generation to meet its electricity needs resulted in system operating problems similar to those experienced during past extreme weather events. Both the high demand for natural gas during cold weather periods and interruptions to the natural gas system have reduced the flow of fuel to generating units, and the natural gas units with dual-fuel capability have not always been effective or timely in switching to using oil. More so, LNG supplies, while beneficial, have been subject to competition from growing worldwide demand. Lastly, infrequently operated coal-fired and oil-fired generators have experienced diminished operating performance and constrained energy production due to issues with fuel availability, delivery, and other challenges caused by the sporadic operation of the units.

The results of studies, as well as actual events, demonstrate the need for fuel certainty in the region. The results of an ICF International study show that the region is projected to have shortfalls of natural gas supply during winter periods through 2020, even with the addition of 450 million cubic feet per day (MMcf/d) of new pipeline capacity. Planned and forced outages of non-gas-fired generation (e.g., nuclear and coal units) further increase the system’s reliance on gas-fired generation and its exposure to potential shortfalls of natural gas for fueling this electric power generation. The retirement of older coal, oil, and nuclear units and their replacement, in whole or in part, with generators that burn natural gas is expected to increase the regional dependence on natural-gas-fired generation to provide electric energy and capacity. Additionally, force majeure events (e.g., caused by weather, equipment failures, fuel embargos, and labor strikes) could interrupt all types of fuel supplies and further complicate the fuel-certainty issue.

To address the fuel-certainty issue, generators and other contracting entities can make firm commitments for procuring natural gas. This would lead to the improved use of existing natural gas infrastructure as well as infrastructure upgrades, such as the addition of natural gas pipelines and LNG terminals, which in turn would improve the deliverability of natural gas. Several infrastructure improvements have been proposed, and the New England states are considering additional means of funding new pipeline capacity into the region. Hydroelectric power can be accessed by building transmission interconnections with Canada, for which the states also are considering a means of funding. Proposed Elective Transmission Upgrades (ETUs), in various stages of development, could improve access to renewable resources in neighboring areas and remote areas of New England. The ISO’s Strategic Transmission Analysis and economic study results also stated that adding transmission facilities to areas of northern New England could facilitate access to large-scale wind power, if developed in this region, and be extended to support imports of Canadian hydropower.

Greater fuel diversity would also improve system reliability. This could be achieved through the more effective use of dual-fuel-capability at existing dual-fuel units and incentives that encourage the development of this capability at existing non-dual-fuel units and proposed single-fueled units. During winter 2013/2014, resource performance and fuel-adequacy issues were improved through a winter reliability program and better coordination between electric power and natural gas system operations. FERC has approved an ISO program for winter 2014/2015, revised from the 2013/2014 program.

Environmental and economic incentives provided by governmental policies are encouraging the development of low-emitting, renewable resources, such as wind and solar. These resources could diversify the fuel supply; however, the reliable large-scale integration of intermittent resources would place increased regulation and reserve requirements on the system, presenting challenges for operating and planning the system. Conventional and pumped-storage hydroelectric facilities have traditionally been well suited to provide regulation and reserves, but they may lose some of their operating flexibility as part of their relicensing requirements. Natural gas units, which are subject to gas nomination and physical constraints, and baseload units, particularly nuclear units, which are normally dispatched to their maximum output, also are unsuitable for helping meet regulation and reserve requirements. Increasing the availability of operating reserves, enhancing market incentives, and procuring sufficient resources to meet the region’s ramping and regulation needs all would improve system flexibility, and several recent and planned market improvements are aimed at addressing these issues.

Although most photovoltaic resources do not require transmission expansion, for these resources to be integrated into the system while maintaining system reliability, their interconnection requirements must be revised and their operational forecast tools improved. Operating procedures may need to be revised, as well, to address unique operating requirements associated with a larger composition of intermittent resources in the capacity mix. In addition, smart grid technologies presently being developed and implemented should improve the electric power system’s performance and operating flexibility.

Transmission projects have been placed in service throughout the region, and others are in various stages of development, including siting. The required timing and components of certain projects are being modified, however, because of the reduction in net loads, the retirement of generating resources, and the addition of new market resources. In general, the development of resources in load pockets relieves transmission system constraints. But when resources fail to develop in the required amounts and in the needed locations, properly timed transmission projects that provide access to more remote resources are critical for meeting regional reliability requirements and mitigating the risks associated with resource deficiencies.

The ISO has coordinated interregional planning activities with the New York Independent System Operator (NYISO), PJM Interconnection, neighboring Canadian provinces, and multiregional organizations, such as NPCC and NERC, and has actively participated in the Eastern Interconnection Planning Collaborative (EIPC). The ISO has filed with FERC proposed measures required for compliance with Order No. 1000 that will change interregional planning and interregional transmission cost allocation.

## Major Findings and Observations

This section highlights the major findings and observations of the RSP14 load forecast, energy-efficiency forecast, and photovoltaic forecast; supply and demand resource and transmission planning studies; market outcomes; and economic studies. Other projects, studies, and initiatives affecting the system planning process are summarized. The sections of the report that contain more details of these findings and observations are indicated.

For all RSP14 analyses, the ISO used a number of assumptions, which are subject to uncertainty over the course of the planning period. Changes in these assumptions may vary RSP14 results and conclusions of the analyses and ultimately can influence the future development of transmission and generation and demand resources:

Fuel availability and fuel-price forecasts, which change with world markets and infrastructure development

Demand and energy-efficiency forecasts, which are dependent on the economy, new building and federal appliance-efficiency standards, state EE goals and program implementation, and other considerations

Resource availability, which is dependent on physical and economic parameters that affect the performance, development, and retirement of resources

Environmental regulations and compliance strategies, which can vary with changes in public policies, economic parameters, and technology development

The deployment of new technologies, which may affect the physical ability and the economic viability of new and existing resources and the efficiency of operating the power system

Market rules and public policies, which can alter the development of market resources and renewable resources

Timing of planned system improvements, which can be subject to siting and construction delays, and other changes to the system

The ISO considers these factors for developing a comprehensive and flexible plan. While each RSP is a snapshot in time, the ISO updates the results of planning activities as needed, accounting for the status of ongoing projects, studies, and new initiatives.

### Forecasts of Peak Demand, Annual Use of Electric Energy, Effects of Energy-Efficiency Measures, and Distributed Generation

RSP14 includes forecasts of annual and peak energy use, as well as the peak load reductions and annual energy savings from energy efficiency. The amount and location of the net system load affect the need for new resources and the required timing of some transmission projects.

#### Peak Demand, Annual Use of Electric Energy, and Load Growth

The RSP14 forecast of summer peak demand is lower than the RSP13 forecast by 125 MW for 2014 and by 205 MW for 2022 for the 50/50 “reference” case. The RSP14 50/50 summer peak forecast is 28,165 MW for 2014, which grows to 31,620 MW for 2023. The 90/10 summer peak forecast, which represents more extreme summer heat waves, is 30,470 MW for 2014 and increases to 34,195 MW in 2023. The ISO forecasts the 10-year growth rate to be 1.3% per year for the summer peak demand, 0.6% per year for the winter peak demand, and 1.0% per year for the annual use of electric energy. The annual load factor (i.e., the ratio of the average hourly load during a year to peak hourly load) continues to decline from 56.1% in 2014 to 54.7% in 2023. (Section 3.1.1)

Load forecasts are highly dependent on the economic forecast, which reflects economic trends. The RSP14 load forecasts also account for reductions based on the historical growth of non-FCM energy-efficiency savings and the expected effects of federal EE standards for appliances and commercial equipment. The load forecast does not include the energy-efficiency savings of the passive demand resources (PDRs) that participate in the Forward Capacity Market or account for the energy-efficiency forecast. These PDRs and the energy-efficiency forecast are represented as supply-side resources in planning studies. (Section 3.1.2)

#### Energy-Efficiency Forecast

RSP14 discusses the annual planned additions of EE in the FCM for 2014 through 2017 and forecasts new EE for each year from 2018 to 2023. The EE forecast (for 2018 through 2023) shows a regionwide annual average energy savings of approximately 1,518 gigawatt-hours (GWh) and an average reduction in peak loads of 205 MW per year. The EE forecast shows savings from new energy efficiency levels (i.e., not cumulative EE) of 1,764 GWh in 2018, ranging to 1,288 GWh in 2023. Similarly, the peak load savings from new EE ranges from 239 MW in 2018 to 174 MW in 2023. The EE forecast also shows results for each New England state. (Section 3.2)

The annual energy-use forecast, minus both the FCM passive demand resources projected for 2014–2017 and the 2018–2023 energy-efficiency forecast, shows essentially no net long-run growth in electric energy use and would save 13.8% of the forecasted gross energy consumption in 2023. The summer peak 90/10 forecast, when adjusted for both the existing FCM PDRs projected for 2014–2017 and the 2018–2023 energy-efficiency forecast, is projected to increase at 0.7% compared with the 1.3% projected growth rate of the demand forecast. Transmission planning studies use this adjusted 90/10 forecast, and at 30,873 MW for 2023, is 747 MW lower than the gross 50/50 forecast of 31,620 MW. After allowing for FCM energy efficiency and the EE forecast, the winter peak demand is expected to slightly decline at a rate of 0.1% over the 10-year forecast. (Section 3.3)

#### Distributed Generation Forecast

Distributed generation resources have been rapidly growing in New England and are predominantly photovoltaic resources developed as a result of governmental policies (e.g., incentives). To be able to account for the rapid growth of PV resources and their intermittent performance, the ISO, with input from the six New England states and other stakeholders, developed a multistate forecast of PV. The forecast considers the amounts and locations of existing PV resources, state policy objectives for PV development, and uncertainties in future policy and market and price conditions necessary to support the continued development of PV.

By the end of 2013, the installed nameplate of PV was almost 500 MWAC, which was approximately double the amount installed in 2012. The PV forecast also shows an increase of PV resources to over 1,800 MWAC by 2023, which has a total estimated summer seasonal claimed capability (SSCC) of approximately 632 MW. Almost 70% of PV is projected to be in Massachusetts. (Section 3.4)

The growth in distributed generation resources, particularly PV resources, poses extraordinary technical challenges for grid operators and planners, some of which are as follows:

A limited amount of DG resource data for planning studies, including resource size, location, and operational characteristics

A current inability of system operators to observe and control DG resources in real time

A need to better understand the impacts of growing DG on system operations, including ramping, reserve, and regulation requirements for the most intermittent resources

Potential reliability impacts to the regional power system posed by future amounts of DG, resulting from existing state interconnection standards

- The challenges are being addressed through advanced research conducted by the US Department of Energy (DOE) and highly technical analysis by ISO staff. Stakeholder discussions have provided vital data and guidance to the ISO.

- The ISO is working to improve its operating forecasts to more fully account for PV. The ISO also plans on improving the PV planning forecast, producing a PV energy forecast for RSP15, and more fully addressing the above issues and other challenges presented by the growth of DG resources. Additionally, the ISO and stakeholders are discussing the use of the PV forecast in long-term planning studies, and progress has been evident over the past year; economic studies have already considered the modeling of PV resources, and plans call for using the PV forecast in new transmission planning studies. Stakeholder discussions on the use of the PV forecast in other planning studies, such as resource adequacy studies, will continue in fall 2014, with plans for implementation by FCA #10.

Although the ISO is not directly involved with the interconnection of most distributed generation and traditionally has not been aware of the timing or locations of DG installations, in the planning process, it considers existing DG as resources or as part of the historical load, which is an input into the ISO load forecast. The ISO will continue discussions with stakeholders to develop any needed improvements required to extend the planning forecast from PV to other types of DG as a part of RSP15.

### Needs for Capacity and Operating Reserves

RSP14 quantifies the system needs for capacity and operating reserves and the amounts procured through the Forward Capacity Market and the locational Forward Reserve Market (FRM).

#### Capacity

The minimum amount of capacity the region needs to meet resource adequacy requirements is called the Installed Capacity Requirement (ICR). The region’s net ICR is expected to grow from 32,588 MW in 2014 to a representative value of 36,100 MW by 2023. This represents a growth of approximately 390 MW per year, which is equivalent to 1.14% per year. The development of generation, demand, and import capacity resources for the region is required to provide the capacity needed to meet the ICR. Because the ICR calculation accounts for the load-relieving actions of ISO Operating Procedure No. 4 (OP 4), Action during a Capacity Deficiency, meeting the ICR level could necessitate the use of specific OP 4 actions. Several factors affect the frequency and extent of OP 4 actions, including the amount of resources procured to meet capacity needs, their availability, actual system loads, and other system conditions. Study results show that the need for load and capacity relief by OP 4 actions will be as much as 2,665 MW during extremely hot and humid summer peak-load conditions over the planning horizon. (Section 4.1)

FCA #8 resulted in the first capacity shortage in a primary auction. As recently as fall 2013, a surplus of capacity resources (both new and existing) was considered likely for the auction, but retirements have since been announced. Resources will be procured for the 2017/2018 capacity commitment period if deemed necessary in upcoming annual reconfiguration auctions. The region is projected to require 424 MW in 2019/2020, which would increase to a shortage of 1,155 MW in 2023/2024, accounting for the load and energy-efficiency forecasts and only known retirements. This also assumes all resources with capacity supply obligations for FCA #8 remain in service. In August 2013, Entergy announced the retirement of Vermont Yankee (604 MW) and submitted a nonprice retirement request. During fall 2013, the ISO received nonprice retirement requests for an additional 2,531 MW to leave the market. The ISO analyzed 100 “static” delist bids, totaling 4,170 MW, and was not required to reject any for reliability reasons in FCA #8. The probability for resource retirements at future auctions will likely accelerate the need for new resources; the region already is beginning to lose older, relatively inefficient generating facilities. Additionally, generation owners could choose not to invest in environmental remediation measures called for in pending or required regulations, which could force these units to shut down. (Sections 4.1)

The amount of capacity resources located in import-constrained zones is projected to meet the local resource adequacy requirements. Connecticut resources exceed this zone’s local sourcing requirement (LSR) by 1,872 MW. In FCA #8, the LSR for Northeast Massachusetts (NEMA)/Boston was 3,428 MW, and the resources in this area, including new resources not yet on line, totaled 3,821 MW. Although the NEMA/Boston area is projected to have surplus capacity, the ISO has growing concerns about the lack of timely development of new resources in this area that, if not developed, would result in the area being short of required capacity. Additional load growth or reduced resource availability—possibly resulting from fuel supply issues; a failure to develop new, cleared resources in a timely manner; or retirements—could create the need to develop additional new resources across the region or in constrained zones . (Section 4.1.3)

FERC-approved changes also will improve the market incentives for developing resources when and where needed, and the Strategic Planning Initiative is assessing ways to enhance the efficient development of resources. The ISO is following a new two-step process for creating, modifying, or collapsing capacity zones. Step one identifies potential zonal boundaries and associated transfer limits. Step two uses objective criteria to evaluate the portions of the system identified in step one and establish whether any of these areas will be modeled as capacity zones in the capacity auction. These changes are addressing the relationship between the zonal reconfigurations and the ISO’s rejection of delist bids. A new zone for the Southeast Massachusetts/Rhode Island (SEMA/RI) area will be eligible for modeling in FCA#9. In general, the development of new resources near the system load centers mitigates reliability risks associated with resource retirements and resource performance issues, improves system performance, and allows for improved use of the existing transmission infrastructure. Resources in the generator interconnection queue, which included 6,915 MW as of April 1, 2014; new demand resources; and new import capacity from neighboring regions are in various stages of development and could address some of these issues. (Sections 4.5)

#### Operating Reserves and Resource Flexibility

Operating reserve is the megawatt capability of a power system greater than system demand required for preserving system reliability—such as by providing frequency regulation, responding to load forecast errors, and filling the void left by forced outages—when resources or transmission facilities are lost because of a contingency. Some resources are required to be synchronized to the system for immediate use (i.e., spinning resources), and some must be fast-start resources. In New England, resources participating in the locational FRM and other committed and on-line resources help satisfy the operating-reserve requirements of the region overall and in major load pockets.

The ISO develops the representative operating-reserve requirements of major import areas as ranges to account for future uncertainties about the availability of resources, load variations due to weather, and other factors. For 2014 through 2018, the representative operating-reserve requirements for Greater Southwest Connecticut is from 0 to 350 MW. Over the same period, the need for operating reserves in Greater Connecticut is as much as 1,100 MW during the summer, and similarly, the need for the BOSTON area is as much as 350 MW. Although each of these areas currently has sufficient resources to meet its representative reserve requirements, the placement of fast-start, energy-efficiency, and economical baseload resources in these load pockets would improve system performance. Transmission projects that increase the transfer capability into these areas or in other ways improve the electrical access of these areas to economical resources also would enhance the economical and reliable performance of the system.

The need for flexible resources to provide operating reserves as well as other ancillary services, such as regulation and ramping, will likely increase as a result of unit retirements and the addition of variable energy resources, particularly wind and PV. To date, increasing the 10-minute operating-reserve requirement and adding seasonal replacement reserves have improved the systemwide performance for meeting peak load, ramping during changing system conditions, and the resource response to contingencies. (Section 4.3)

### Transmission System Needs and Solutions

Transmission projects placed in service have reduced congestion and decreased dependence on generating units located in load pockets. In 2013, the real-time systemwide congestion-related costs totaled approximately $175,000, and payments for generators in “must-run” situations that provided second-contingency coverage and voltage control totaled just under $54.6 million. These values in total represent approximately 0.6% of the $8.82 billion wholesale electric energy market. (Sections 5.6 and 5.8.2)

#### Transmission Projects

The ISO and the PAC regularly discuss the scope of transmission system needs and the progress of assessments that drive regional transmission planning for improvements. The PAC provides guidance and comments on study scopes, assumptions, and results. All transmission projects are coordinated with other regions as warranted. The ISO also has advised the PAC of the regional network service (RNS) rate and projections developed by the PTOs. (Section 5.3)

The descriptions of transmission projects in RSP14 are based on the June 2014 RSP Project List update, which includes 222 projects at a total cost of approximately $4.5 billion. The ISO updates the RSP Project List at least three times per year, identifying improvements and changes in project status. The status of several major projects under development is as follows: (Section 5.4)

- The Maine Power Reliability Program (MPRP), for which the Maine Public Utilities Commission (MPUC) has approved siting for most of the components, establishes a second 345 kilovolt (kV) path in northern Maine from Surowiec to Orrington and adds new 345 kV lines in southern Maine, creating a third parallel path from Surowiec to Eliot. Many components of these new paths are under construction, and several elements already are in service. When completed, they will provide basic infrastructure needed to increase the ability to move power from New Hampshire into Maine and will improve the ability of the transmission system within Maine to move power into the local load pockets as necessary. Studies have demonstrated that the MPRP also will provide a modest increase in the transfer capability across major interfaces in Maine, including an increase from 1,600 to 1,900 MW of the Maine-to-New Hampshire transfer capability. The MPRP project is scheduled for completion by early 2015, with the exception of upgrades around Lewiston expected to be complete by January 2017.

- The New England East–West Solution (NEEWS) series of projects has been identified to address system reliability needs:

- The Rhode Island components and the Springfield components of NEEWS were placed in service in 2013.

- The Interstate Reliability Project (IRP) was reevaluated in light of updated load and energy-efficiency forecasts; system operating constraints; and resources acquired, delisted, or retired through the Forward Capacity Auctions, such as Salem Harbor. Consistent with the original plan, the final plan calls for a new 345 kV transmission between Millbury, MA; West Farnum, RI; Lake Road, CT; and Card, CT. Additional system modifications to the original plan have been identified, which primarily relieve thermal constraints. Other improvements identified in the original plan have been eliminated, including upgrades to 345 kV facilities. The IRP has received siting approval and is under construction.

- A reevaluation of the Central Connecticut Reliability Project (CCRP), a 345 kV line from North Bloomfield to Frost Bridge, has been completed with the Greater Hartford/Central Connecticut study. A number of 115 kV upgrades that address local Hartford concerns and issues associated with imports into western Connecticut have replaced the CCRP project.

- The Long-Term Lower Southeastern Massachusetts (Lower SEMA) project addresses system reliability concerns in the lower southeastern Massachusetts (LSM) area, which includes Cape Cod, and went into service in 2014. The project included adding a new 345 kV transmission line from the Carver substation to a new 345/115 kV substation west of Barnstable on Cape Cod, adding a third 345 kV line serving Cape Cod.

- The Greater Boston study assessed and identified improvements required to respect revised cable ratings in downtown Boston and the addition of Footprint Power generating plant (674 MW) at the Salem Harbor site. The ISO is reviewing the merits of two alternatives, which include an independent review of the cost of each alternative to ensure that the most cost-effective solution is selected for the Greater Boston area. One alternative includes new 345 kV circuits from Scobie to Tewksbury and from Wakefield to Woburn, and the other alternative plan includes a high-voltage, direct-current (HVDC) submarine cable (SeaLink HVDC Submarine Cable Project) extending from Seabrook, New Hampshire, to Boston, Massachusetts. System improvements common to both alternatives also were identified.

In addition to the system needs assessments and solutions studies, several major transmission planning studies have been completed, and others are underway to address system issues in all six New England states. Some studies have developed preferred solutions to serve major portions of the system, including Vermont and New Hampshire, the southwestern area of Connecticut, the Berkshire County/Pittsfield area of western Massachusetts, and the Southeast Massachusetts/Rhode Island area. All studies examine the system comprehensively and account for the electrical characteristics of the tightly integrated New England network. The ISO continues to review the elements and timing of projects throughout the system to account for changes in load level, resource development and availability, and other factors.

Resources help ensure the reliability of area load pockets, which include portions of Maine, the Boston area, southeastern Massachusetts, western Massachusetts, the Springfield area, and portions of Connecticut. In addition to enhancing reliability, transmission improvements placed in service have generally reduced the costs associated with second-contingency and voltage-control payments to generators. The Lower SEMA short-term upgrades are one example of transmission upgrades that have improved reliability, reduced dependencies on generating units, and reduced “make-whole” payments to market participants whose resources had operating costs higher than their energy market revenues over a 24-hour dispatch day. (Section 5.6)

Transmission expansion may be needed to meet future challenges facing the New England region, for preserving the reliability of service to those areas of the system that could face generator retirements within the planning horizon and addressing reliability needs attributable to load growth and resource integration. (Section 5.8)

#### Development of Elective Transmission Upgrades

Several developers have proposed Elective Transmission Upgrades, which are in various stages of study and development. These projects could increase New England’s tie capability with its neighbors and improve access to renewable sources of energy. For example, certain generators are considering elective upgrades as a way to mitigate the curtailment of wind energy resources. The ISO will continue to monitor the outcomes of these upgrades and their impacts on system conditions and needs. The ISO has initiated an effort to improve the existing process for reviewing ETUs. (Section 5.8)

### Regional Strategic Planning

The ISO is assessing a number of potential reliability effects of the fuel-procurement strategies of natural-gas- and oil-fired generators and the influences of public policies, including environmental initiatives. Fuel availability and certainty for generating electric energy, and the system’s need for specific amounts, types, and locations of resources and transmission improvements, are important elements of system reliability being assessed. The ISO also is addressing issues concerning the development and integration of renewable resources and smart grid technologies.

#### Resource Performance and Fuel Certainty

Several strategic planning issues associated with fuel certainty and resource performance stem from the region’s dependence on natural gas-fired generation and other constrained-energy resources. These problems have been quantified, and infrastructure and market solutions are being implemented.

Natural Gas Dependency. New England is increasingly dependent on natural gas as a primary fuel for generating electric energy and decreasing its dependence on oil. In 2013, the approximate percentages of the region’s generation capacity and electric energy production by fuel type were as follows:

- Natural gas: 42.8% capacity and 45.1% electric energy

- Oil: 22.3% capacity and 0.9% electric energy

- Coal: 7.2% capacity and 5.6% electric energy

- Nuclear: 14.6% capacity and 33.2% electric energy

- Hydro, pumped storage, and renewable resources: 13.1% capacity and 15.3% electric energy

The high regional dependence on natural-gas-fired generation has resulted in natural gas fuel prices typically setting the marginal price for wholesale electricity. (Section 6.1)

The high regional use of natural gas to generate electricity is the result of the addition of new, efficient natural-gas-fired units over the past 13 years; the generally low price of natural gas; and the displacement of older, less efficient oil- and coal-fired units in economic dispatch. As the revenues from the wholesale electricity markets decline for these older oil and coal units and more units retire, the regional reliance on natural gas for providing capacity and energy will increase. Natural gas-fired generation’s proportion of the system capacity mix is expected to grow to approximately 48% as early as 2017. The region will continue to depend on natural-gas-fired generation because of the risks faced by other types of generation. Nuclear and hydro units have already announced retirements or may not be relicensed. Many units do not have dual-fuel capability. Other units with dual-fuel capability, especially newer combined-cycle generators, are not effective in terms of the amount of time they need to switch to using oil or the availability of secondary fuel inventory.

Adding to the concern about the increased use of natural gas are concerns about the capacity of the region’s gas pipelines and the adequacy of the gas supply for serving electric power generation reliably; at any time of the year, a natural or geopolitical event could interrupt supplies of gas and other fuels, such as oil and coal. Renewable resources provide some diversity of energy supply but are weather dependent, typically need thermal or hydro resources to accommodate their variability, and pose both interconnection and operational challenges. (Sections 6.2.2 and 6.6)

Natural Gas Infrastructure. Recent improvements to the interregional natural gas infrastructure have helped increase the supply of natural gas from the Marcellus Shale production areas, displacing the Northeast’s traditional supply sources, such as the Gulf of Mexico. Additional enhancements to the regional pipeline network are planned and would allow New England to access the larger quantities of natural gas for the region’s power generators. Further expansion, however, is likely required, which would improve fuel certainty for the electric power system and provide access to more economical natural gas supply. Unlike the electric power industry, which proactively plans the expansion of the transmission network, natural gas transportation requires firm contractual arrangements before natural gas pipeline facilities can be constructed. The New England states are considering the means of funding pipeline expansion into the region, including possible modifications to the ISO tariff. The increased use of existing LNG storage capability or the expansion of this capability also could improve fuel certainty. (Section 6.2.1)

Resource Performance. Operational experience during winter 2013/2014 showed the need for the ISO to manage the limitations of energy production by electric power generators. The vulnerabilities and limitations of the system were evident during severe winter weather and other stressed system conditions because natural gas was not available to generators at desired levels. Several oil-fired generators, which operated periodically and were exposed to equipment failure, fuel interruptions, and supply limitations, further highlighted reliability issues. Market rules that allow resources to constrain their operation when they have limited fuel, such as when the capacity of the natural gas pipeline is lacking, added to operating concerns. (Section 6.2.2)

The ISO has taken a number of actions to address fuel-certainty issues in the short and longer terms. Regional load was reliably served during winter 2013/2014 as a result of improved communication between electric power and natural gas system operators and the successful implementation of a winter reliability program, which proved vital in maintaining required fuel supplies. The ISO has filed and FERC has approved an update to this program for winter 2014/2015. In addition, the ISO is actively collaborating with stakeholders to improve the Day-Ahead Energy Market, Real-Time Energy Market, and Forward Capacity Market. By the end of 2014, the ISO plans on implementing rule changes that allow generators to better reflect the real-time price of fuel in their supply offers. Longer-term, an FCM pay-for-performance mechanism should create stronger financial incentives for capacity supplies to produce electricity and supply reserves when needed the most. This planned market improvement is designed to encourage generator owners to invest in dual-fuel capability or new fast-start assets, enter into firmer fuel arrangements, and have more reliable operating and maintenance practices, which all should in turn reduce the need for stop-gap measures like a winter reliability program.

More fully integrating demand resources into the energy market also is planned to broaden the conditions under which demand resources could be called on to help meet the region’s energy needs. (Section 6.2.2)

Studies of Natural Gas Supply Issues. Planning studies of regional natural gas issues quantified the need to bolster the region’s natural gas system supply or the use of non-gas-fired resources under a number of scenarios. The scenarios included outages of non-gas-fired generating units, the replacement of older oil- and coal-fired generating units with natural-gas-fired generators, and outages of natural gas infrastructure affecting reliable electric power operation. The studies examined the potential natural gas available to the region from pipelines, peak-shaving capabilities of the local distribution companies (LDCs) that serve retail customers, and LNG storage. The natural gas supply was compared with the natural gas demand of firm contract holders, including LDCs. The scenarios considered the demands of natural gas customers upstream of New England, and some modeled the low levels of LNG stored and available to the region during winter 2013/2014. The studies, which used 20 years of weather data, show that electric power generators would likely have a gas supply deficit on 24 to 34 days per winter by 2019/2020. Under 2013/2014 winter conditions, the supply deficit would be even more severe. (Section 6.2.3)

The ISO also is coordinating an interregional study of the natural gas system with the NYISO, PJM, the Midcontinent Independent System Operator (MISO), the Independent Electricity System Operator (of Ontario) (IESO), and the Tennessee Valley Authority (TVA). (Section 6.2.3)

#### The Potential Impacts of Environmental Regulations on the Power System

Existing and pending state, regional, and federal environmental requirements addressing air pollution, greenhouse gas emissions, cooling water drawn from rivers and bays, and wastewater discharges that flow back into these bodies of water as well as public treatment works will affect many New England generators in the 2015 to 2023 timeframe. Many generators in the region already have installed the needed controls to comply with existing state environmental rules, and new transmission upgrades have reduced the need to use older, less efficient oil- and coal-fired units to address more local reliability concerns. These changes, and the greater reliance on natural gas for power generation, have reduced regional air pollution emissions and thermal discharges into the region’s waterways.

Between 2001 and 2012, the annual average emission rate of nitrogen oxides (NOX) declined by 67%; sulfur dioxide (SO2), by 92%; and carbon dioxide (CO2), by 23%. The decrease appears attributable to declines in both oil- and coal-fired generation combined with a significant increase in natural gas generation, which has a substantially lower SO2 emission rate. Future regional emissions could increase however, even with more stringent regulations, if oil-fired generating units need to operate during periods of natural gas shortages or because nuclear units have retired or are on outages. Emissions could decrease with the use of lower-emitting fuels, additional environmental controls, and the greater use of energy efficiency and wind and photovoltaic resources. (Sections 6.3 and 6.4)

The ISO has been assessing the potential impact of existing and proposed US Environmental Protection Agency (EPA) and state regulations on the operation of existing fossil steam units and other types of generation in the region. Uncertainty remains over the extent to which the final regulations will require generator owners to make capital investments in environmental remediation measures and potentially increase plant operating costs. These factors could require long-term generator outages for implementing required remediation measures. They also could trigger unit retirements as an alternative to accepting higher capital and operating costs. Alternatively, generators may comply with some of the environmental requirements by reducing capacity or energy production.

ISO analyses will continue to update stakeholders regarding the generators at risk for retirement and generators that already have environmental remediation measures in place or may require relatively minor upgrades. The actual compliance timelines will depend on the timing and substance of the final regulations and site-specific circumstances of the electric generating facilities, such as their economic performance.

#### Renewable Portfolio Standards and the Integration of Renewable Resources

Renewable Portfolio Standards (RPSs) and similar state goals are stimulating the need for, and the development of, renewable resources and energy efficiency in the region. Other regional and industry efforts are assisting in integrating renewable resources, demand resources, and smart grid technologies into the system.

Meeting State Targets for Renewable Energy. The New England states have targets for the proportion of electric energy that load-serving entities (LSEs) must serve using renewable resources, such as wind, solar, and energy efficiency. Because the states are revising these targets to reflect different amounts and types of resources that qualify for RPSs, the ISO cannot project the precise amount of regional renewable energy goals. The region’s RPSs can be met by developing the renewable resources already in the ISO queue; importing renewable resources from adjacent balancing authority areas; building new renewable resources in New England not yet in the queue; and using “behind-the-meter” projects and eligible renewable fuels, such as biomass, at existing generators. If the development of renewable resources falls short of providing sufficient Renewable Energy Certificates (RECs) to meet the RPSs, load-serving entities can make state-established alternative compliance payments (ACPs). ACPs also can serve as a price cap on the cost of the RECs. (Section 7.5.7)

Integrating Intermittent Renewable Resources. A number of wind projects have interconnected to electrically remote and weak portions of the regional power system, and additional wind projects are proposed for these areas. These facilities pose operational and planning challenges due to issues with voltage and stability performance. In addition, the basic assumptions in interconnection studies may be different from the typical operation of the system, which may further constrain wind output under stressed system conditions, such as during maintenance outages. The ISO is considering ways of improving the Elective Transmission Upgrade process to more readily support the means to strengthen electrically weak portions of the regional transmission network, enhance generator deliverability, and facilitate the integration of renewable resources. (Section 6.6)

The ISO continues to analyze wind-integration issues and has made progress implementing wind forecasting and dispatch. The wind-integration component of the Strategic Transmission Analysis is exploring conceptual modifications to the transmission system that would enable onshore wind resources to more reliably provide energy. This analysis of approximately 1,100 MW of installed and proposed wind resources examined the proposed transmission system as of October 2013. The study identified the need for local area improvements to accommodate the wind resource interconnections and the need for regional transmission improvements to accommodate the total development of wind resources in several regions of Maine. (Section 6.6.2)

The results show that local transmission upgrades could likely accommodate additional wind resource interconnections planned for the Wyman Hydro and Rumford regions in Maine but without major transmission improvements to those local areas. However, additional wind capacity cannot be well integrated into the Keene Road and Bangor regions, also in Maine, without major transmission improvements to these areas. The addition of generation to the Aroostook region of Maine also would require new major transmission facilities to successfully interconnect these resources and integrate them with the rest of the New England system. Regional improvements would be needed to accommodate resources remote from the New England load centers, such as the total wind resources in all the northern New England regions. These transmission improvements could include a major dynamic voltage device, 345 kV dynamically acting series-compensating devices, and 115 kV capacitors.

The 2011 Economic Study quantified the amounts of congestion associated with different wind-penetration scenarios. The results of the study show the effects of integrating varying amounts of wind on production cost, load-serving energy expense, and congestion, as well as the need for transmission development to enable wind resources to serve the region’s load centers. The ISO will continue to engage stakeholders on the issues challenging the wind-interconnection process and the performance of the system with wind resources in locally constrained areas. (Section 6.8.1)

While existing amounts of PV have yet to have a significant impact on system operations, the regional goal is to have over 2,000 MW of distributed generation by 2023, approximately 1,800 MW of which is expected to be PV. The ISO and stakeholders are working on several initiatives aimed at facilitating the reliable and efficient integration of PV, including improving the long-term forecast of the amounts and locations of PV resources and the amount of electric energy PV resources produce; developing a short-term solar forecast for use by system operators; and addressing other potential reliability risks posed by growing penetrations of PV, such as interconnection requirements. (Section 3.4 and 6.7)

Developing New England’s Smart Grid. In general, smart grid technologies can improve the ability of the transmission system to operate reliably under a wide variety of system conditions. They can improve the ability of system operators to observe and control the system, increase the transfer capability of the transmission system while adding less new infrastructure, and facilitate end-user response to the power system. Specific applications of smart grid technologies in New England use demand resources to provide ancillary services, such as operating reserves, and help integrate variable renewable resources, such as wind and photovoltaic power and hydroelectric power from neighboring Canadian regions. Smart grid technologies also can facilitate the reduction in demand when electricity prices are high. This smart grid equipment helps implement both customers’ load response and the use of behind-the-meter resources, such as rooftop solar installations. (Section 7.4.2)

The region is a leader in the smart grid application of HVDC facilities and flexible alternating-current transmission systems (FACTS), which improve the use of system infrastructure. The ISO and the New England transmission owners installed phasor measurement units (PMUs) and associated equipment at 40 substations to upgrade the monitoring and operation of the system. The ISO and stakeholders have also supported research and development efforts and the establishment of industry standards for integrating smart grid technologies, including dispatching active demand resources, which are affected by the installation of smart meters and changes in retail rate structures. Alternative technology regulation resources and active demand resources may be used to provide regulation and reserve services, which would facilitate the reliable integration of intermittent renewable resources. The ISO will continue to monitor the development of and will support the implementation of these and other advanced technologies. (Section 7.4.2)

#### Economic Studies of Resource Integration and Interregional Coordination

Both the 2011 Economic Study and the 2012 Economic Study analyzed several of the strategic issues the region is addressing. The 2011 Economic Study, summarized above, examined the economic and environmental impacts of wind integration. The 2012 Economic Study highlighted the least suitable locations for unit retirements and the most suitable locations for developing different resources without causing congestion. The study showed the effects of using various amounts of energy efficiency and low-emitting resources, including renewable energy.

These studies showed several key results. Accessing the onshore wind energy located in northern New England remote from load centers will require transmission expansion. Replacing older high-emitting coal- and oil-fired units with cleaner-burning natural gas generation will decrease environmental emissions but further increase New England’s dependence on natural gas. The addition of resources with low energy costs decreases electric energy expenses for LSEs but also decreases energy market revenues to resources, which may then require increases in other revenue sources to remain economically viable. (Section 6.8.1)

The ISO conducted an economic study in response to a stakeholder request received in 2013. This study examined the effects of increasing the acceptable loss-of-source limits in New England, which currently is limited by constraints in New York and PJM. The study considered changes in required operating reserves and varying profiles and prices of imported energy. As with other economic studies, the results show changes in the production cost, LSE expenses, and environmental emissions. In general, importing more-economical energy from Canada could lower system energy locational marginal prices (LMPs) and emissions but would increase the cost of operating reserves.

#### Analysis of Market Resources in Load Pockets as an Alternative to Transmission Investment

Results of the Strategic Transmission Analysis show that developing resources integrated into or interconnected to the buses in the Hub or in load pockets is beneficial, especially the load pockets with exposure to potential generator retirements. However, assessing the suitability of developing individual resources can be challenging during the planning process because of the wide variability of the characteristics, locations, and possible combinations of resources that could be developed, such as central station and DG resources, end-use efficiency, and storage technologies. In response to PAC requests for more details about resources that could meet system needs, the ISO applied the lessons learned from studies of the Vermont/New Hampshire area and the Greater Hartford/Central Connecticut area to a study of Southeast Massachusetts/Rhode Island (SEMA/RI). The study respected the contingency loss of power system elements (N-1 criteria contingencies) but did not address constraints respecting subsequent criteria contingencies (N-1-1 criteria contingencies) and FCM deliverability requirements. The analysis considered large generators (greater than or equal to 20 MW), small generators (less than 20 MW), and demand resources (less than 40% of the load at a given location). The results show that a minimum of 941 MW of total new generation and load reductions ranging from 5 MW to 590 MW at specific locations, as well as some minor transmission upgrades, can mitigate the thermal and voltage needs for the area. (Section 6.10)

### Interregional Planning

ISO New England’s planning activities are closely coordinated at the state, regional, interregional, and federal levels. Identifying interregional system needs and the potential impacts that proposed generating units and transmission projects could have on neighboring systems is beneficial to support interregional reliability and economic performance.

The ISO has developed coordinated system plans and has proactively initiated planning studies with other regions. The ISO has worked with both NYISO and PJM through the Northeastern ISO/RTO Planning Coordination Protocol and issued the 2013 Northeast Coordinated System Plan (NCSP13) that addresses several key interregional issues and summarizes key activities. The ISO/RTOs have coordinated databases and models of their systems and conducted production cost analyses and transmission analyses of planned system improvements and interconnections. The three planning authorities have discussed these studies and key planning issues affecting the Northeast with stakeholders. Some of these issues include environmental regulations and their potential effect on the power system, challenges and solutions facilitating the integration of renewable resources, the need for fuel diversity, and the results of coordinated studies of the natural gas system. (Section 7.1)

Sharing more supply and demand resources with other systems most likely will be needed, particularly to meet environmental regulations and successfully integrate intermittent resources. The ISO has worked with stakeholders to establish a means of complying with FERC Order No. 1000, which includes changing the interregional planning process and interregional cost allocation. ISO New England will continue conducting joint studies with NYISO and PJM to identify transmission constraints limiting interregional power transfers and to show the effects of relieving these constraints throughout the ISO/RTO regions. The ISO also will continue to coordinate other efforts with neighboring systems to explore the ability to import power from, and export power to, the eastern Canadian provinces and New York and participate in national and regional planning activities.

ISO New England and other planning authorities throughout the Eastern Interconnection are members of the Eastern Interconnection Planning Collaborative. The EIPC addresses its portion of North American planning issues, coordinates plans, and conducts studies for the entire Eastern Interconnection through a transparent and collaborative process involving input from a broad base of interested stakeholders. ISO New England also serves as a principal investigator for a project funded as part of DOE grant work. At DOE’s request, EIPC is studying how the interface between the natural gas and electric power systems affects operations and planning. In a separate effort, the EIPC is also coordinating planning databases and conducting scenario analyses of electric power transmission systems for the entire Eastern Interconnection. (Sections 7.1.1 and 7.2)

The ISO participates in several other national and regional system planning forums, such as NERC, the ISO/RTO Council, and the NPCC. Through the NPCC and NERC, the ISO has participated in interregional assessments, which coordinate planning studies and demonstrate compliance with all required planning standards, criteria, and procedures.

### State, Regional, and Federal Initiatives that Affect System Planning

The ISO continuously works with a wide variety of state policymakers and other regional and interregional stakeholders on initiatives such as the Strategic Planning Initiative. Regional initiatives continue for improving the wholesale electricity markets, integrating new technologies, and documenting the regional transmission planning process and technical requirements for planning studies. The draft Transmission Planning Process Guide and the draft Transmission Planning Technical Guide will be revisited to align with final Order No. 1000 requirements. In response to stakeholder requests, the ISO is also continuing to work with stakeholders to examine suitable assumptions for use in planning studies, which may more fully consider the probability of resources outages, system transfers, and system load levels.

The ISO has continued to provide technical support to a number of state agencies and groups as they formulate policies for the region. These groups include the New England Conference of Public Utilities Commissioners (NECPUC), the New England States Committee on Electricity (NESCOE), the New England governors, the Consumer Liaison Group (CLG), and others. The planning process will continue to evolve in response to FERC orders and other policy developments. The Quadrennial Energy Review by DOE, which will conclude in 2015, is a comprehensive analysis of energy and electricity production and delivery systems that addresses the challenges of cyber- and physical security of critical infrastructure. (Section 7.3)

## Conclusions

The 2014 Regional System Plan identifies system needs and plans for meeting these needs. RSP14 also discusses risks to the regional electric power system; the likelihood, timing, and potential consequences of these risks; and mitigating actions. Through an open process, regional stakeholders and the ISO are addressing these issues, which could include further infrastructure development as well as changes to the wholesale electricity market design and the system planning process. Through current and planned activities, the region is working toward meeting all challenges for planning and operating the system in accordance with all requirements.

# Introduction

As the Regional Transmission Organization (RTO) for New England, ISO New England (ISO) operates the region’s electric power system, administers the region’s competitive wholesale electricity markets, and conducts the regional system planning process, which includes coordinating planning efforts with neighboring areas. The main objectives of the ISO’s system planning process are as follows:

- Identify system needs and potential solutions for ensuring the short-term and long-term reliability of the system

- Facilitate the efficient operation of the markets through resource additions and transmission upgrades that serve to reliably move power from various internal and external sources to the region’s load centers

- Provide information to regional stakeholders, who can further develop system improvements

To meet these objectives and in compliance with all portions of the ISO’s Transmission, Markets, and Services Tariff (ISO tariff), including the Open Access Transmission Tariff (OATT), the 2014 Regional System Plan (RSP14) describes the ISO’s ongoing system resource and transmission planning activities covering the 10-year period to 2023.

This section provides an overview of RSP14 and the ISO’s regional system planning process required by the ISO’s tariff. For background, the section also provides highlights of the power system and the wholesale electricity market structure in New England. A summary of the various regional subdivisions the ISO uses in system planning studies also is provided.

Throughout RSP14, italicized terms indicate that a definition for the term is included within the text or footnotes; links to other documents that more fully define the more complex terms are provided. Links to relevant technical reports; presentations; and other, more detailed materials also are included throughout the report. All website addresses are current as of the time of publication. Appendix A is a list of acronyms and abbreviations used in RSP14.

## Overview of the System Planning Process and RSP14

To assess how to maintain the reliability of the New England power system, while promoting the operation of efficient wholesale electricity markets, the ISO and its stakeholders analyze the system and its components as a whole. They account for the performance of these individual elements and the many varied and complex interactions that occur among the components and that affect the overall performance of the system. The major steps in planning the regional electric power system are as follows:

- Forecasting the peak demand for electric energy and the average annual use of electric energy

- Forecasting the amount of energy efficiency (EE) that will be available and determining the potential effect of energy efficiency on system peak demand

- Assessing the amounts and general locations of resources that the overall system and individual areas of the system need, the types of resources that can satisfy these needs, and any critical time constraints for addressing resource needs

- Analyzing transmission system needs and developing potential solutions to meet these needs

- Assessing scenarios of the economic performance of the system with existing resources, possible resource retirements, and potential resource development

- Coordinating study efforts with surrounding RTOs, balancing authority areas, and the entire Eastern Interconnection and analyzing information and data presented in neighboring plans through a number of interregional agreements and joint studies

Using information on defined system needs, a variety of established signals from ISO-administered markets, and other factors, stakeholders responsible for developing needed resources can assess their options for satisfying these needs and commit to developing market resource projects. For example, stakeholders can build a new power plant to provide additional system capacity and electric energy production or provide active demand resources and passive demand resources (PDRs) to reduce the amount of electric energy used. They also can develop Elective Transmission Upgrades (ETUs).

These elective transmission and supply and demand resource alternatives could result in modifying, offsetting, or deferring proposed regulated transmission upgrades. To the extent that stakeholder responses to market signals are not forthcoming or adequate to meet identified system needs, the planning process requires the ISO to conduct subsequent planning of regulated transmission upgrades to meet the identified needs.

The draft Transmission Planning Process Guide and draft Transmission Planning Technical Guide describe the transmission planning process and the assumptions used with transmission planning studies in more detail. The ISO will revise these documents to be consistent with changes in the planning process required by the Federal Energy Regulatory Commission’s (FERC) Order No. 1000 (see Sections 7.2.1 and 7.4.3).

### Planning Studies Conducted for and Summarized in RSP14

The ISO conducts numerous regional and local-area studies throughout the year during all stages of planning for ensuring the reliability of the power system. FERC, interregional entities, the states, and others, also sponsor planning initiatives for improving the power system and interregional coordination. RSP14 summarizes the ISO’s major studies and initiatives, as well as those conducted by others, both individually and jointly with the ISO, including the following:

- Ten-year load forecasts through 2023 of peak demand and the average annual use of electric energy (Section 3.1)

- Regional energy-efficiency (EE) forecast from 2018 to 2023 (Section 3.2)

- A forecast of photovoltaic (PV) (i.e., solar) development in the region and plans for the development of a distributed generation (DG) forecast in general (Section 3.4)

- Analyses of the amount, operating characteristics, and locations of needed capacity and operating reserves (Section 4)

- Assessments of systemwide and local-area needs (i.e., needs assessments) that include critical load levels, and transmission solutions to meet these needs (i.e., solution studies) (Section 5)

- Studies assessing regional strategic planning needs and solutions, including studies in support of the ISO’s Strategic Planning Initiative (SPI), which address the following topics: (Section 6)

- Resource performance and fuel certainty, including power system operating experience and the operation and infrastructure of the natural gas system

- Operating and planning for expansion of renewable resources, including the potential need for transmission development for wind generation and the identification of interconnection issues for distributed generation

- Effect of generator compliance with environmental regulations on generator retirements

- Implications of generator retirements on transmission system requirements and potential locations for developing new resources (i.e., the Strategic Transmission Analysis)

- Simulations of the estimated economic and environmental performance of various future resource- and transmission-expansion scenarios (Section 6.8)

- 2011, 2012, and 2013 Economic Studies

- Analysis of capacity and energy supply needs

- Planning coordination studies and other activities (Section 7)

- Northeastern ISO/RTO planning coordination studies

- Eastern Interconnection Planning Collaborative activities

- Other joint planning studies with neighboring regions

- ISO initiatives and governmental activities and policies affecting the planning the system

### Other Planning Considerations

The regional system planning process, which complies with all requirements, involves working closely with stakeholders and exchanging detailed information with them about the system. Another consideration for planning the system is making sure ISO studies and underlying assumptions account for the ever-changing physical and market forces that can affect the system and system plans.

#### Working with the Planning Advisory Committee and Other Committees

To conduct the system planning process, the ISO holds an open and transparent stakeholder forum with the Planning Advisory Committee (PAC). PAC membership is open to all and currently includes representatives from state and federal governmental agencies; participating transmission owners (PTOs); ISO market participants; other New England Power Pool (NEPOOL) members; consulting companies; manufacturers; and other organizations, such as universities and environmental groups. The PAC has met 15 times from fall 2013 to summer 2014 to discuss draft scopes of work, assumptions, and draft and final study results on a wide range of issues. In addition, subgroups of the PAC have discussed the energy-efficiency forecast, environmental issues, and the distributed generation forecast.

Other committees are involved in the system planning process. The Reliability Committee (RC) provides advisory input on planning procedures, final proposed plan applications, regional transmission cost allocations, and other activities that affect the design and oversight of reliability standards for the power system. The Transmission Committee provides advisory input on the general tariff provisions of the OATT and amendments to the Transmission Owner Agreement. The Markets Committee provides advisory input on changes proposed by the ISO to Market Rule 1 and market procedures. Stakeholders who advise ISO New England or its neighboring ISO/RTOs on system planning matters have the opportunity to meet as a unified group through the Interregional Planning Stakeholder Advisory Committee (IPSAC).

#### Providing Information to Stakeholders

In addition to publishing the Regional System Plan and specific needs assessments and solutions studies to provide information to stakeholders, the ISO issues the RSP Project List, which includes the status of transmission upgrades during a project’s lifecycle and is updated several times per year (see Section 5.3). RSP14 incorporates information from the June 2014 list. Additionally, the ISO posts on its website detailed information supplemental to the RSP process, such as the Annual Markets Report (AMR), Wholesale Markets Project Plan (WMPP), presentations, and other reports. The ISO also makes available databases used in its analyses and related information required to perform simulations consistent with FERC policies and the ISO Information Policy requirements pertaining to both confidential information and critical energy infrastructure information (CEII) requirements. Stakeholders can use this information and data to conduct their own independent studies.

#### Accounting for Uncertainty

Regional system planning must account for the uncertainty in assumptions made about the next 10 years stemming from changing demand, fuel prices, technologies, market rules, planning processes, and environmental requirements; the development and retirement of resources; the physical conditions under which the system might be operating; and other relevant events. The following major factors may vary RSP14 results and conclusions and ultimately affect the development and timing of needed transmission facilities and generation, demand, and market resources:

Forecasts of demand, energy efficiency, and distributed generation, which are dependent on the economy, new building and federal appliance-efficiency standards, state goals for the implementation of energy-efficiency and distributed-generation programs, and other considerations

Resource availability, which is dependent on physical and economic parameters that affect the performance, development, and retirement of resources

Environmental regulations and compliance strategies, which can vary with changes in public policies, economic parameters, and technology development

The deployment of new technologies, which may affect the physical ability and the economic viability of new types of power system equipment and the efficiency of operating the power system

Fuel price forecasts, which change with world markets and infrastructure development

Market rules and public policies, which can alter the development of market resources

The timing of planned system improvements, which can be subject to siting and construction delays, uncertainty due to the implementation of the competitive process for transmission development under FERC Order No. 1000, and changes to the system

While each RSP represents a snapshot in time, the planning process is continuous, and the results are revisited as needed when new information becomes available.

#### Meeting All Requirements

In addition to complying with the ISO tariff, which reflects the requirements of FERC orders, RSP14 complies with North American Electric Reliability Corporation (NERC) and Northeast Power Coordinating Council (NPCC) criteria and standards, as well as ISO planning and operating procedures. RSP14 also conforms to transmission owner criteria, rules, standards, guides, and policies consistent with NERC, NPCC, and ISO criteria, standards, and procedures. RSP14 reflects the impacts that federal government and New England state policies have on system planning. The region is awaiting a ruling on the FERC Order No. 1000 compliance filings.

## Overview of the New England Electric Power System

New England’s electric power grid has been planned and operated as a unified system of its participating transmission owners and market participants. The New England system integrates resources with the transmission system to serve all regional load regardless of state boundaries. Most of the transmission lines are relatively short and networked as a grid. Therefore, the electrical performance in one part of the system affects all areas of the system. Figure 2-1 shows key facts about the New England regional electric power system.

|  | - 6.5 million households and businesses; population 14 million - Approximately 350 generators - Approximately 31,000 MW of total generation for 2014 - Over 8,500 miles of transmission lines - 13 interconnections to electricity systems in New York and Canada - Approximately 2,100 MW of demand resources for 2014 - All-time peak demand of 28,130 MW, set on August 2, 2006 - Approximately 500 participants in the marketplace (those who generate, buy, sell, transport, and use wholesale electricity and implement demand resources) - Market value in 2013: - $8.82 billion total - $7.49 billion energy market - $1.06 billion capacity market - $0.27 billion ancillary services market - Approximately $6.5 billion in transmission investment since 2002; approximately $4.5 billion planned |
| --- | --- |

Figure 2-1: Key facts about New England’s electric power system and wholesale electricity markets.

Source: The 2014–2022 Forecast Report of Capacity, Energy, Loads, and Transmission (CELT 2014) (May 2014), http://www.iso-ne.com/system-planning/system-plans-studies/celt; the RSP Project List for June 2014; and the 2013 Annual Markets Report.

Notes: The 2,100 MW of ISO demand resources do not include energy efficiency provided by other customer-based programs outside the ISO markets or are otherwise unknown to the ISO. The total load on August 2, 2006, would have been 28,770 MW had it not been reduced by approximately 640 MW, which included a 490 MW demand reduction in response to ISO Operating Procedure No. 4 (OP 4), Action during a Capacity Deficiency; a 45 MW reduction of other interruptible OP 4 loads; and a 107 MW reduction of load as a result of price-response programs, which are outside of OP 4 actions. (OP 4 guidelines contain 16 actions in total that can be implemented individually or in groups, depending on the severity of the situation.) More information on OP 4 is available at http://www.iso-ne.com/static-assets/documents/rules_proceds/operating/isone/op4/op4_rto_final.pdf.

## Overview of the New England Wholesale Electricity Market Structure

New England’s wholesale electricity markets facilitate the buying, selling, and transporting of wholesale electricity, as well as ensure proper system frequency and voltage, sufficient future capacity, seasonal and real-time reserve capacity, and system restoration capability after a blackout. Stakeholders also have the opportunity to hedge against the costs associated with transmission congestion. As shown in Figure 2-1, in 2013, approximately 500 market participants completed transactions in New England’s wholesale electricity markets totaling $8.82 billion. The wholesale electricity markets and market products in New England are as follows:

- Day-Ahead Energy Market—allows market participants to secure prices for electric energy the day before the operating day and hedge against price fluctuations that can occur in real time.

- Real-Time Energy Market—coordinates the dispatch of generation and demand resources to meet the instantaneous demand for electricity.

- Forward Capacity Market (FCM)—ensures the sufficiency of installed capacity, which includes demand resources, to meet the future demand for electricity by sending appropriate price signals to attract new investment, maintain existing investment, and encourage capacity to perform both where and when needed, including during shortage events.

- Financial Transmission Rights (FTRs)—allows participants to hedge against the economic impacts associated with transmission congestion and provides a financial instrument to arbitrage differences between expected and actual day-ahead congestion.

- Ancillary services

- Regulation Market—compensates resources that the ISO instructs to increase or decrease output moment by moment to balance the variations in demand and system frequency to meet industry standards.

- Forward Reserve Market (FRM)—compensates generators for the availability of their operational capacity not generating electric energy but able to be converted into electric energy within 10 or 30 minutes when needed to respond to system contingencies, such as unexpected outages.

- Real-time reserve pricing—compensates participants with on-line and fast-start generators for the increased values of their electric energy when the system or portions of the system are short of reserves. It also provides efficient price signals to generators when redispatch is needed to provide additional reserves to meet requirements.

- Voltage support—compensates resources for maintaining voltage-control capability, which allows system operators to maintain transmission voltages within acceptable limits.

One key feature of the region’s wholesale electricity markets is locational marginal pricing for electric energy, which reflects the variations in supply, demand, and transmission system limitations effectively at every location where electric energy enters or exits the wholesale power network. In New England, wholesale electricity prices are set at over 1,000 pricing points (i.e., pnodes) on the power grid. If the system were entirely unconstrained and had no losses, all locational marginal prices (LMPs) would be the same, reflecting only the cost of serving the next megawatt increment of load by the generator with the lowest-cost electric energy available, which would be able to flow to any point on the transmission system. LMPs would differ among the pnodes if each location’s marginal cost of congestion and marginal cost of line losses differed.

Transmission system constraints, which limit the flow of the least-cost generation and create the need to dispatch more costly generation, give rise to the congestion component of an LMP. Line losses are caused by physical resistance and subsequent heat loss in the transmission system as electricity travels through transformers, reactors, and other types of equipment, resulting in less power being withdrawn from the system than was injected. Line losses and their associated marginal costs are inherent to transmission lines and other grid infrastructure as electric energy flows from generators to loads. As with the marginal cost of congestion, the marginal cost of losses affects the amount of generation that must be dispatched. The ISO operates the system to minimize total system costs, while recognizing physical limitations of the system.

## Overview of System Subdivisions Used for Analyzing and Planning the System

To assist in modeling, analyzing, and planning electricity resources in New England, the region and the system have been subdivided in various ways. These categories are included in the discussions throughout the RSP and are summarized below.

The system’s pricing points include individual generating units, load nodes, load zones (i.e., aggregations of load pnodes within a specific area), and the Hub. The Hub is a collection of 32 locations in central New England where little congestion is evident. It typically has a price intended to represent an uncongested price for electric energy, which is used as a price index and point of exchange for bilateral transactions in the energy market. The Hub also facilitates energy trading and enhances transparency and liquidity in the marketplace. In New England, generators are paid the LMP for electric energy at their respective nodes, and participants serving demand pay the price at their respective load zones.

New England is divided into eight electric energy load zones used for wholesale energy market settlement: Maine (ME), New Hampshire (NH), Vermont (VT), Rhode Island (RI), Connecticut (CT), Western/Central Massachusetts (WCMA), Northeast Massachusetts and Boston (NEMA), and Southeast Massachusetts (SEMA). Import-constrained load zones are areas within New England that do not have enough local resources and transmission-import capability to serve local demand reliably or economically. Export-constrained load zones are areas within New England where the available resources, after serving local load, exceed the areas’ transmission capability to export the excess electric energy. Reliability regions, which reflect the operating characteristics of, and the major constraints on, the New England transmission system, can have the same boundaries as load zones.

A capacity zone is a geographic subregion of the New England Balancing Authority Area that may represent load zones that are export constrained, import constrained, or contiguous—neither export nor import constrained. Capacity zones are used in the Forward Capacity Auctions (FCAs) and are subject to annual review. The capacity zones for FCA #8 were Maine, Connecticut, NEMA/Boston, and “Rest-of-Pool” (i.e., the area excluding the other zones) (see Sections 4.1.2 and 4.1.3). On April 28, 2014, FERC approved an updated methodology for evaluating and modeling capacity zones, which will be in place for FCA #9, scheduled for February 2015. The region also currently has four reserve zones—Greater Connecticut; Greater Southwest Connecticut (SWCT); NEMA/Boston; and the rest of the system (Rest-of-System, ROS), which excludes the other, local reserve zones.

Additionally, the region is divided into 19 demand-resource dispatch zones, which are groups of nodes used to dispatch real-time demand-response (RTDR) resources or real-time emergency generation (RTEG) resources. These allow for a more granular dispatch of active demand resources at times, locations, and quantities needed to address potential system problems without unnecessarily calling on other active demand resources. Figure 2-2 shows the dispatch zones the ISO uses to dispatch FCM active demand resources.

Figure 2-2: Active-demand-resource dispatch zones in the ISO New England system.

The ISO also has established 13 subareas of the region’s electric power system. These subareas form a simplified model of load areas connected by the major transmission interfaces across the system. The simplified model illustrates possible physical limitations to the reliable and economic flow of power that can evolve over time as the system changes.

Figure 2-3 shows the ISO subareas and three external balancing authority areas. While transmission planning studies and the real-time operation of the system use more detailed models, the subarea representation shown in Figure 2-3 is suitable for some RSP14 studies of production cost and environmental emissions.

|  | Subarea Designation | Region or State |
| --- | --- | --- |
|  | BHE | Northeastern Maine |
|  | ME | Western and central Maine/ Saco Valley, New Hampshire |
|  | SME | Southeastern Maine |
|  | NH | Northern, eastern, and central New Hampshire/eastern Vermont and southwestern Maine |
|  | VT | Vermont/southwestern New Hampshire |
|  | Boston (all capitalized) | Greater Boston, including the North Shore |
|  | CMA/NEMA | Central Massachusetts/ northeastern Massachusetts |
|  | WMA | Western Massachusetts |
|  | SEMA | Southeastern Massachusetts/ Newport, Rhode Island |
|  | RI | Rhode Island/bordering Massachusetts |
|  | CT | Northern and eastern Connecticut |
|  | SWCT | Southwestern Connecticut |
|  | NOR | Norwalk/Stamford, Connecticut |
|  | NB, HQ, and NY | New Brunswick (Maritimes), Hydro­Québec, and New York external balancing authority areas |

Figure 2-3: RSP14 geographic scope of the New England electric power system.

Notes: Some RSP studies investigate conditions in Greater Connecticut, which combines the NOR, SWCT, and CT subareas. This area has similar boundaries to the State of Connecticut but is slightly smaller because of electrical system configurations near the border with western Massachusetts. Greater Southwest Connecticut includes the southwest and western portions of Connecticut and consists of the NOR and SWCT subareas. NB includes New Brunswick, Nova Scotia, and Prince Edward Island (i.e., the Maritime provinces) plus the area served by the Northern Maine Independent System Administrator (USA).

# Forecasts of New England’s Peak Demand, Annual Use of Electric Energy, Energy Efficiency, and Distributed Generation

Load forecasts provide key inputs for evaluating the reliability and economic performance of the electric power system under various conditions and for determining whether and when improvements are needed. This section summarizes the forecasts for the annual use of electric energy and peak loads, New England-wide and in individual states and subareas. It also describes the economic and demographic factors that drive the forecasts and explains the forecasting methodology. For RSP14, the underlying methodology for forecasting annual energy use and peak loads has not changed from RSP13.

Additionally, the section provides the results of the ISO’s regional energy-efficiency (EE) forecast for the 10-year RSP planning horizon. The 2014 EE forecast reduces the peak load and net energy consumption forecasts for New England. The region’s efforts to develop a distributed generation forecast and the results of a forecast of regional and state-by-state photovoltaic capability also are discussed.

## ISO New England Load Forecasts

The ISO load forecasts are estimates of the amount of electric energy the New England states will need annually and during seasonal peak hours. This year’s forecast horizon runs from 2014 through winter 2023/2024. Each forecast cycle updates the data for the region’s historical annual use of electric energy and peak loads by adding another year of data to the sample, incorporating the most recent economic and demographic forecasts, and making adjustments for resettlement that include meter corrections.

Table 3-1 summarizes the ISO’s forecasts of annual electric energy use and seasonal peak load (50/50 and 90/10) for New England overall and for each state. RSP14 forecasts of annual energy use, and both summer and winter seasonal peak conditions are similar to those published in RSP13. Compared with the RSP13 forecast, the RSP14 50/50 load forecast for summer peak demand is 125 MW lower in 2014 and 205 MW lower in 2022.

Table 3-1
Summary of Annual Electric Energy Use and Peak Demand Forecast for New England
and the States, 2014/2015 and 2023/2024

| State(a) | Net Energy for Load (1,000 MWh) |  |  | Summer Peak Loads (MW) |  |  |  |  | Winter Peak Loads (MW) |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | 50/50 |  | 90/10 |  | CAGR(b) | 50/50 |  | 90/10 |  | CAGR(b) |
|  | 2014 | 2023 | CAGR(b) | 2014 | 2023 | 2014 | 2023 |  | 2014/15 | 2023/24 | 2014/15 | 2023/24 |  |
| CT | 34,390 | 37,495 | 1.0 | 7,415 | 8,165 | 8,100 | 8,890 | 1.0 | 5,725 | 5,910 | 5,895 | 6,080 | 0.3 |
| ME | 12,265 | 13,175 | 0.8 | 2,110 | 2,315 | 2,240 | 2,465 | 1.1 | 1,930 | 1,985 | 2,020 | 2,080 | 0.3 |
| MA | 63,875 | 70,525 | 1.1 | 13,060 | 14,860 | 14,070 | 16,000 | 1.4 | 10,380 | 11,040 | 10,645 | 11,305 | 0.7 |
| NH | 12,370 | 13,700 | 1.1 | 2,555 | 2,940 | 2,745 | 3,170 | 1.6 | 2,055 | 2,210 | 2,175 | 2,330 | 0.8 |
| RI | 8,755 | 9,455 | 0.9 | 1,920 | 2,150 | 2,165 | 2,430 | 1.3 | 1,410 | 1,445 | 1,450 | 1,485 | 0.3 |
| VT | 6,730 | 7,175 | 0.7 | 1,100 | 1,190 | 1,145 | 1,240 | 0.9 | 1,080 | 1,145 | 1,135 | 1,200 | 0.6 |
| New England | 138,390 | 151,525 | 1.0 | 28,165 | 31,620 | 30,470 | 34,195 | 1.3 | 22,575 | 23,735 | 23,325 | 24,480 | 0.6 |

- A variety of factors cause state growth rates to differ from the overall growth rate for New England. For example, Connecticut has the fastest-growing economy in New England, and Maine has the slowest-growing economy in the region.

- “CAGR” stands for compound annual growth rate.

Net energy for load (NEL) is the generation output within an area, accounting for electric energy imports from other areas and electric energy exports to other areas. It also accounts for system losses and excludes the electric energy used to operate pumped-storage hydroelectric plants. The compound annual growth rate (CAGR) for the ISO’s electric energy use is 1.0% for 2014 through 2023, 1.3% for the summer peak, and 0.6% for the winter peak. The systemwide load factor (i.e., the ratio of the average hourly load during a year to peak hourly load) declines over the forecast horizon, from 56.1% in 2014 to 54.7% in 2023 and begins to flatten by the end of forecast.

Figure 3-1 shows a comparison of the ISO’s actual summer peak demand (i.e., the load reconstituted to include the megawatt reduction attributable to ISO New England Operating Procedure No. 4 [OP 4], Action during a Capacity Deficiency, and FCM passive demand resources) with the 50/50 load forecast and with the 90/10 load forecast. The actual load has been near or has exceeded the 90/10 forecast six times over the last 22 years because of hot and humid weather conditions, and it has been near or above the 50/50 forecast 11 times during the same period.

Figure 3-1: The ISO’s actual summer peak loads (i.e., reconstituted for OP 4 and FCM passive demand resources) and the 50/50 and 90/10 forecasts, 1992 to 2013 (MW).

Note: The forecasted load values are the first-year values of the CELT forecast for each year. For example, the forecasted loads for 2013 are the loads for the first year of the 2013 CELT Report.

### Economic and Demographic Factors and Electric Energy Use

The price of electricity and other economic and demographic factors drive the annual consumption of electric energy and the growth of the seasonal peak. In addition to net energy for load, the forecasts account for the effects of future federal long-term energy-efficiency goals, as well as the historical effects of energy efficiency, but they do not reflect the peak and electric energy savings attributable to passive demand resources in the FCM market and the future EE forecast (see Section 3.1.2). Similarly, the forecast of annual consumption and growth of the seasonal peak considers existing distributed generation not otherwise counted as a resource.

The ISO’s forecasts of electric energy use in New England and each state are based on a total energy-use concept, which sums the amount of electric energy used residentially (about 39%), commercially (about 38%), and industrially (about 23%). Real gross state product (RGSP) serves as a proxy for overall economic and demographic conditions. This variable is the primary force driving the model of electric energy use. Table 3-2 summarizes these and other indicators of the New England economy.

Table 3-2
New England Economic and Demographic Forecast Summary

| Factor | 1980 | 2013 | CAGR | 2014 | 2023 | CAGR |
| --- | --- | --- | --- | --- | --- | --- |
| Summer peak (MW) | 14,539 | 27,835 | 2.0 | 28,165 | 31,620 | 1.3 |
| Net energy for load (1,000 MWh) | 82,927 | 137,193 | 1.5 | 138,390 | 151,525 | 1.0 |
| Population (thousands) | 12,404 | 14,616 | 0.5 | 14,659 | 14,964 | 0.2 |
| Real price of electricity (¢/kWh, 2013$)(a) | 17.901 | 14.431 | −0.7 | 14.431 | 14.431 | 0.0 |
| Employment (thousands) | 5,483 | 6,987 | 0.7 | 7,070 | 7,450 | 0.6 |
| Real income (millions, 2005 $) | 298,071 | 744,927 | 2.8 | 776,146 | 963,640 | 2.4 |
| Real gross state product (millions, 2005 $) | 310,370 | 737,680 | 2.7 | 759,890 | 933,624 | 2.3 |
| Energy per household (MWh) | 18.860 | 23.824 | 0.7 | 23.847 | 24.722 | 0.4 |
| Real income per household (thousands) (2005 base year) | 67.789 | 129.356 | 2.0 | 133.745 | 157.221 | 1.8 |

        - The forecast of the retail electricity prices assumes that the nominal price of electricity will grow at the rate of inflation (or with flat real prices from 2013 to 2023) and fully incorporate the capacity costs from the Forward Capacity Market. “kWh” stands for kilowatt-hour.

The Economy.com November 2013 economic forecast of real gross state product was used to represent overall economic activity in the RSP14 forecast models. Compared with the November 2012 Economy.com economic forecast, the November 2013 Economy.com forecast of real gross state product shows slower growth from 2011 through 2014, higher growth in 2015, and similar growth for the remaining years. Both forecasts show a slow recovery from the recession, which affects the load forecast. Figure 3-2 compares the RGSP forecasts from November 2013 with those from November 2012.

Figure 3-2: “Economy.com” forecasts of New England gross state product from November 2013 and November 2012 forecasts.

Source: Moody’s Analytics, Economy.com.

Notes: Years 1981 to 2013 reflect actual gross state product. Note the Bureau of Economic Analysis (of the US Department of Commerce) revisions to the historical data for 2007 to 2013.

### The CELT Forecast and Passive Demand Resources

The seasonal peak load and energy-use forecast, as published in the 2014–2023 Forecast Report of Capacity, Energy, Loads, and Transmission (2014 CELT Report) and used for calculating the Installed Capacity Requirement (ICR), fully accounts for historical energy efficiency, passive demand resources, and future federal appliance standards. The forecast does not expressly reflect the future reduction in peak demand and energy use that will result from the passive demand resources that clear the Forward Capacity Auctions. Similarly, the energy-efficiency forecast (described in Section 3.2) is a separate forecast that is not included as part of the peak load and energy-use forecast. Historical reductions in load from “other demand resources” (ODRs) in the transition period leading up to the FCM and from the passive demand resources in the FCM have been added back into the historical loads used for load forecasting.

### Subarea Use of Electric Energy

Much of the RSP14 reliability and production cost analysis depends on the forecasts of annual electric energy use and peak demand in the subareas. Table 3-3 summarizes these forecasts and provides important market information to stakeholders. Table 3-4 shows the forecast for the RSP subareas and their relationship to the load zones and states. The forecasts for the peak demand and annual energy use in the subareas are derived by first allocating the ISO’s state forecasts to distribution companies within the states on the basis of historical shares; second, allocating the distribution company forecasts to busses using the ISO model of the transmission network; and finally, aggregating the busses for each of the subareas.

Table 3-3
Forecasts of Annual Use of Electric Energy and Peak Demand in RSP Subareas, 2014 and 2023

| Area | Net Energy for Load (1,000 MWh) |  |  | Summer Peak Loads (MW) |  |  |  |  | Winter Peak Loads (MW) |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | 50/50 Load |  | 90/10 Load |  |  | 50/50 Load |  | 90/10 Load |  |  |
|  | 2014 | 2023 | CAGR | 2014 | 2023 | 2014 | 2023 | CAGR | 2014/15 | 2023/24 | 2014/15 | 2023/24 | CAGR |
| BHE | 1,785 | 1,915 | 0.8 | 305 | 335 | 325 | 360 | 1.1 | 280 | 290 | 295 | 305 | 0.4 |
| ME | 5,775 | 6,210 | 0.8 | 950 | 1,040 | 1,010 | 1,110 | 1.1 | 950 | 975 | 995 | 1,025 | 0.3 |
| SME | 4,380 | 4,710 | 0.8 | 785 | 865 | 830 | 920 | 1.2 | 660 | 680 | 690 | 710 | 0.3 |
| NH | 10,595 | 11,625 | 1.0 | 2,170 | 2,470 | 2,330 | 2,665 | 1.5 | 1,750 | 1,865 | 1,850 | 1,970 | 0.7 |
| VT | 7,850 | 8,520 | 0.9 | 1,355 | 1,505 | 1,425 | 1,585 | 1.2 | 1,270 | 1,360 | 1,335 | 1,430 | 0.8 |
| BOSTON | 28,845 | 31,960 | 1.1 | 5,905 | 6,745 | 6,360 | 7,260 | 1.5 | 4,685 | 5,000 | 4,805 | 5,120 | 0.7 |
| CMA/NEMA | 8,445 | 9,095 | 0.8 | 1,710 | 1,895 | 1,840 | 2,040 | 1.2 | 1,385 | 1,445 | 1,420 | 1,480 | 0.5 |
| WMA | 10,850 | 11,890 | 1.0 | 2,155 | 2,440 | 2,320 | 2,630 | 1.4 | 1,810 | 1,905 | 1,855 | 1,950 | 0.6 |
| SEMA | 14,225 | 15,495 | 1.0 | 2,975 | 3,360 | 3,215 | 3,630 | 1.4 | 2,260 | 2,360 | 2,320 | 2,420 | 0.5 |
| RI | 11,705 | 13,130 | 1.3 | 2,535 | 2,910 | 2,815 | 3,240 | 1.6 | 1,880 | 2,025 | 1,935 | 2,080 | 0.8 |
| CT | 16,410 | 18,215 | 1.2 | 3,540 | 3,970 | 3,865 | 4,320 | 1.2 | 2,735 | 2,870 | 2,820 | 2,950 | 0.5 |
| SWCT | 11,085 | 12,195 | 1.1 | 2,390 | 2,655 | 2,610 | 2,890 | 1.1 | 1,850 | 1,925 | 1,905 | 1,980 | 0.4 |
| NOR | 6,440 | 6,570 | 0.2 | 1,390 | 1,430 | 1,515 | 1,560 | 0.3 | 1,065 | 1,035 | 1,095 | 1,065 | −0.3 |
| ISO total(a, b) | 138,390 | 151,525 | 1.0 | 28,165 | 31,620 | 30,470 | 34,195 | 1.3 | 22,575 | 23,735 | 23,325 | 24,480 | 0.6 |

(a) 	The total load-zone projections are similar to the state load projections and are available at the ISO’s “2014 Forecast Data File,” http://www.iso-ne.com/static-assets/documents/trans/celt/fsct_detail/2014/isone_fcst_data_2014.xls; tab #2, “ISO-NE Control Area, States, Regional System Plan (RSP14) Subareas, and SMD (Standard Market Design) Load Zones Energy and Seasonal Peak-Load Forecast.”

(b) 	Totals may not equal the sum because of rounding and may not exactly match the results for other tables in this section.

Table 3-4 
Forecasts of RSP Subarea Peak Demand, 2014(a)

| RSP Subarea | Load Zone | State | 50/50 Summer Peak Load |  |  | 90/10 Summer Peak Load |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | MW | % of RSP Subarea | % of State | MW | % of RSP Subarea | % of State |
| BHE | ME | Maine | 305.0 | 99.7 | 14.5 | 325.0 | 100.1 | 14.5 |
| ME | ME | Maine | 950.0 | 99.9 | 45.0 | 1,010.0 | 100.1 | 45.1 |
| SME | ME | Maine | 785.0 | 100.1 | 37.2 | 830.0 | 99.7 | 37.1 |
| NH | ME | Maine | 70.0 | 3.2 | 3.3 | 75.0 | 3.2 | 3.3 |
|  | NH | New Hampshire | 2,060.0 | 94.9 | 80.6 | 2,215.0 | 95.1 | 80.7 |
|  | VT | Vermont | 40.0 | 1.8 | 3.6 | 45.0 | 1.9 | 3.9 |
|  |  |  | 2,170 |  |  | 2,330 |  |  |
| VT | NH | New Hampshire | 340.0 | 25.1 | 13.3 | 365.0 | 25.6 | 13.3 |
|  | VT | Vermont | 1,020.0 | 75.2 | 92.7 | 1,060.0 | 74.4 | 92.6 |
|  |  |  | 1,360 |  |  | 1,425 |  |  |
| BOSTON | NH | New Hampshire | 85.0 | 1.4 | 3.3 | 90.0 | 1.4 | 3.3 |
|  | WCMA | Massachusetts | 105.0 | 1.8 | 0.8 | 110.0 | 1.7 | 0.8 |
|  | NEMA/ Boston | Massachusetts | 5,715.0 | 96.8 | 43.8 | 6,160.0 | 96.9 | 43.8 |
|  |  |  | 5,905.0 |  |  | 6,360.0 |  |  |
| CMA/NEMA | NH | New Hampshire | 70.0 | 4.1 | 2.7 | 80.0 | 4.3 | 2.9 |
|  | WCMA | Massachusetts | 1,640.0 | 95.9 | 12.6 | 1,765.0 | 95.8 | 12.5 |
|  |  |  | 1,710 |  |  | 1,845 |  |  |
| WMA | VT | Vermont | 40.0 | 1.9 | 3.6 | 45.0 | 1.9 | 3.9 |
|  | CT | Connecticut | 100.0 | 4.6 | 1.3 | 105.0 | 4.5 | 1.3 |
|  | WCMA | Massachusetts | 2,015.0 | 93.6 | 15.4 | 2,170.0 | 93.5 | 15.4 |
|  |  |  | 2,155 |  |  | 2,320 |  |  |
| SEMA | RI | Rhode Island | 185.0 | 6.2 | 9.6 | 210.0 | 6.5 | 9.7 |
|  | SEMA | Massachusetts | 2,790.0 | 93.8 | 21.4 | 3,005.0 | 93.5 | 21.4 |
|  |  |  | 2,975 |  |  | 3,215 |  |  |
| RI | RI | Rhode Island | 1,735.0 | 68.5 | 90.4 | 1,955.0 | 69.4 | 90.3 |
|  | SEMA | Massachusetts | 800.0 | 31.6 | 6.1 | 860.0 | 30.5 | 6.1 |
|  |  |  | 2,535 |  |  | 2,815 |  |  |
| CT | CT | Connecticut | 3,540.0 | 100.0 | 47.7 | 3,865.0 | 100.0 | 47.7 |
| SWCT | CT | Connecticut | 2,390.0 | 100.0 | 32.2 | 2,610.0 | 100.0 | 32.2 |
| NOR | CT | Connecticut | 1,390.0 | 100.1 | 18.7 | 1,515.0 | 99.9 | 18.7 |

(a) Totals may not equal the sum because of rounding and may not exactly match the results for other tables in this section.

## Energy-Efficiency Forecast for New England

The FCM provides the ISO with a comprehensive understanding of the savings in energy use over the FCM horizon. Since 2009, the ISO also has been analyzing energy-efficiency programs and studying how to model incremental, future EE savings for periods five to 10 years beyond the FCM horizon. This deliberate and analytic effort advanced the ISO’s understanding of energy efficiency from anecdotal to empirical. The result was the nation’s first regional (multistate) long-term forecast of energy efficiency. The ISO’s regional energy-efficiency forecast, as summarized in this section for 2018 through 2023, is part of ongoing efforts to collect and analyze data in support of the long-term impacts of state-sponsored energy-efficiency programs on future demand.

The final EE forecast for 2018 to 2023 projects savings in the average, total, and peak energy use for the region and each state. The results, which are based on an average annual program spending rate among the six states of more than $900 million per year, show that the regional annual average savings in energy use attributable to new energy-efficiency measures (i.e., not cumulative from EE savings before 2018) is 1,518 gigawatt-hours (GWh). The forecast for the total savings in energy use from the EE projected for 2018 to 2023 is 9,105 GWh. The states’ annual average savings in energy use ranges from a low of 68 GWh in New Hampshire to a high of 749 GWh in Massachusetts.

Table 3-5 shows the results of ISO’s final EE forecast for 2018 to 2023. The regional average savings in peak demand grows by 205 MW annually. The forecast for total savings in peak demand grows by 1,233 MW from 2018 to 2023. The states’ annual average peak savings ranges from a low of 11 MW in New Hampshire to a high of 101 MW in Massachusetts.

Table 3-5
 ISO New England’s Final Energy-Efficiency Forecast for 2018 to 2023 (GWh, MW)(a)

| Forecast of Electric Energy Savings (GWh) |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Year | Sum of States | States |  |  |  |  |  |
|  |  | ME | NH | VT | CT | RI | MA |
| 2018 | 1,764 | 142 | 76 | 125 | 401 | 141 | 880 |
| 2019 | 1,658 | 132 | 73 | 120 | 379 | 132 | 823 |
| 2020 | 1,560 | 122 | 69 | 117 | 358 | 123 | 769 |
| 2021 | 1,462 | 114 | 66 | 110 | 338 | 114 | 719 |
| 2022 | 1,373 | 106 | 63 | 106 | 319 | 106 | 672 |
| 2023 | 1,288 | 99 | 60 | 102 | 300 | 99 | 628 |
| Total | 9,105 | 714 | 408 | 681 | 2,096 | 715 | 4,491 |
| Average | 1,518 | 119 | 68 | 113 | 349 | 119 | 749 |
| Forecast of Peak Demand Savings (MW) |  |  |  |  |  |  |  |
| Year | Sum of States | States |  |  |  |  |  |
|  |  | ME | NH | VT | CT | RI | MA |
| 2018 | 239 | 20 | 12 | 18 | 49 | 22 | 118 |
| 2019 | 225 | 19 | 12 | 17 | 46 | 20 | 111 |
| 2020 | 211 | 17 | 11 | 17 | 44 | 19 | 104 |
| 2021 | 198 | 16 | 11 | 16 | 41 | 18 | 97 |
| 2022 | 186 | 15 | 10 | 15 | 39 | 16 | 90 |
| 2023 | 174 | 14 | 10 | 14 | 37 | 15 | 85 |
| Total | 1,233 | 101 | 66 | 96 | 255 | 111 | 605 |
| Average | 205 | 17 | 11 | 16 | 42 | 18 | 101 |

(a) The forecast results are available at www.iso-ne.com/eefwg.

Individual program administrators and state regulatory agencies provide the ISO with the EE program performance and budget data used to create the forecast. ISO New England’s Energy-Efficiency Forecast Working Group assesses the forecast assumptions and offers input.

## Load Forecast Incorporating Results for FCA #8 and the 2014 Energy-Efficiency Forecast

The section presents the load forecast reflecting FCM passive demand resources, including the results of the eighth Forward Capacity Auction (FCA #8) for the 2017/2018 capacity commitment period (CCP) and the 2014 energy-efficiency forecast for 2018–2023. Figure 3-3 and Figure 3-4 show the forecasts of annual energy use and summer peak loads, incorporating FCM-qualified PDRs through 2017 and the EE forecast data for 2018 to 2023.

Figure 3-3: RSP14 annual energy-use forecast (diamond), energy-use forecast minus FCM #8 PDRs through 2017 (square), and energy-use forecast minus FCM PDRs and minus the energy-efficiency forecast (triangle) for 2018 to 2023 (GWh).

Figure 3-4: RSP14 summer peak demand forecast (90/10) (diamond), demand forecast minus FCM #8 PDRs through 2017 (square), and demand forecast minus FCM PDRs and minus the energy-efficiency forecast (triangle) for 2018 to 2023 (MW).

As shown in Table 3-6, the annual energy-use forecast, minus both the FCM-qualified passive demand resources projected for 2014–2017 and the results of the 2018–2023 energy-efficiency forecast, indicates essentially no long-run growth in electric energy use. The summer peak 90/10 forecast, when adjusted for both the existing FCM-qualified PDRs projected for 2014–2017 and the 2018–2023 energy-efficiency forecast, is projected to increase at a more modest rate, approximately half the projected growth rate of the forecast. The net winter peak is flat (i.e., negative 0.1%) over the 10-year forecast.

Table 3-6 
2014 Forecasts of Annual and Peak Electric Energy Use
Compared with the Forecast Minus FCM-Qualified Passive Demand Resources (2014 to 2017)
and Energy-Efficiency Forecast Results (2018 to 2023)

|  | Gross | Gross − (FCM + EEF) |
| --- | --- | --- |
| NEL | 1.0 | 0.1 |
| 50/50 and 90/10 Summer | 1.3 | 0.7 |
| 50/50 and 90/10 Winter | 0.6 | −0.1 |

## Distributed Generation Forecast

Following the success of its energy-efficiency forecast, in 2013 the ISO began to develop a methodology for forecasting the long-term impacts of distributed generation resources in New England. After researching other grid operators’ approaches and establishing an open stakeholder process, the ISO developed the nation’s first multistate forecast of DG resources 10 years into the future. This section describes the creation and scope of this DG forecast. The section also highlights next steps that may broaden the focus of the DG forecast.

### Background

DG resources are growing significantly in New England. Because PV resources constitute the largest segment of DG resources throughout New England, the ISO’s analysis of DG and the creation of the first DG forecast focus exclusively on the impact of anticipated DG photovoltaics.

Across the region, PV is being installed at rapidly increasing rates. Data gathered by the ISO indicate that, starting at relatively low levels in recent years, about 250 MWAC of PV was installed in the region by the end of 2012. By the end of 2013, installed nameplate PV jumped to almost 500 MWAC. State policy drives much of this development. For example, Massachusetts reached its 250 MWDC PV goal four years early in 2013, and in May 2013, the commonwealth announced an expanded in-state PV goal of developing 1,600 MWDC by 2020.

Almost all PV systems interconnect to the distribution system pursuant to state-jurisdictional interconnection standards. Because the ISO is not directly involved in the interconnection of most of these resources, it has not traditionally been aware of when and where they are installed.

To help address the interrelated questions of exactly how much additional PV is anticipated in the ISO’s 10-year planning horizon and what impacts this future PV could have on the regional power grid, the ISO, in conjunction with stakeholders, endeavored to create a forecast of all future PV resources—those that participate in the ISO New England markets as well as those that do not. To assist its development of a DG forecast and provide a forum to discuss DG integration issues, the ISO established the Distributed Generation Forecast Working Group (DGFWG) open to all interested parties. State agency representatives with strong knowledge of DG programs, as well as electric power distribution companies and DG program administrators, play a key role in the DGFWG. The DGFWG’s work and other stakeholder group contributions will build on and contribute to other ISO efforts to address these challenges.

### Development of a PV Forecast Methodology

The creation of a PV forecast is exceptionally complicated. The viability of PV development depends on a complex interaction between both public policy and private investment. The unknown future costs of PV and advances in its technology create additional uncertainties affecting the potential and realizable amounts of PV development. Further, as an intermittent resource (i.e., subject to variations in “fuel” determined by weather), the seasonal and diurnal fluctuations of the solar resource are important considerations. Therefore, the amounts, timing, performance characteristics, and geographic distribution of future PV development are all factors that must be considered in a PV forecast. Working through the DGFWG, the ISO determined that its first step would be to develop a qualitative DG forecast focusing exclusively on PV. Moreover, because of the noted complexities, the PV forecast would be limited to PV that results from New England state policies.

### Data Collection

The first step in developing the PV forecast was the compilation of information on state PV policy goals as a part of the states’ objectives for developing renewable resources. To this end, the ISO surveyed states for details on their specific PV policies, as well as distribution utilities to identify existing amounts of PV resources and those in the ISO Generator Interconnection Queue (the queue).

### PV Forecast

The ISO based its PV estimates on the states’ policy goals and adjusted the megawatt amounts for various factors, including a DC-to-AC nameplate conversion rate (where appropriate) and the application of the tariff-driven summer seasonal claimed capability (SSCC) factor. Importantly, because most states do not have PV-focused policies that extend through the ISO’s 10-year forecast horizon, the ISO assumed that PV would be installed at a constant rate equal to the last available policy year. However, because of significant uncertainty regarding how much PV existing and future PV policies will ultimately support, the ISO-applied discount factors to the PV estimates. The discount factors are in addition to the above-noted adjustment factors.

In general, discount factors are applied to forecast values of policy-supported megawatts of PV, are applied equally in all states, and increase annually—over time, as much as 25%. PV forecasted beyond the existing state program duration is more heavily discounted (75%) because of a much higher degree of uncertainty in forecasting future policy and market/price conditions necessary to support the continued development of PV. Table 3-7 shows the discount factor percentages for state policy-supported megawatts of PV from 2013 to 2023 and for post-policy years for the known policy years. The ISO applied these discount rates to the future projections of PV growth in New England.

Table 3-7
Discount Factor Percentages for New England State Policy-Supported Megawatts of PV,
2013 to 2023 and Post-Policy Years

| Policy-Based MW Percentage |  |  |  |  |  |  |  |  |  |  | Post-Policy MW % |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Through 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 |  |
| 0%, but utility data must confirm | 10% | 15% | 20% | 25% | 25% | 25% | 25% | 25% | 25% | 25% | 75% |

Table 3-8 lists the state-by-state annual and cumulative PV nameplate capacities, after applying discount factors, forecast through the 10-year planning horizon. These projections include all existing and future PV in the FCM, as well as PV that does and does not participate in the ISO’s wholesale energy markets and that reduces the load the ISO observes. The table also lists the corresponding total estimated summer seasonal claimed capability of the annual and cumulative capacities, which assume a 35% AC nameplate-to-SSCC ratio. Solar typically has a zero or negligible winter SCC.

Table 3-8
State-by-State Annual and Cumulative PV Nameplate Capacity Forecast
after Applying Discount Factors, 2013 to 2023 (MWAC)

| States | Annual Total MW (MW, AC nameplate rating) |  |  |  |  |  |  |  |  |  |  | Totals |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Through 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 |  |
| CT | 73.8 | 46.2 | 39.3 | 53.0 | 34.7 | 34.7 | 13.1 | 13.1 | 13.1 | 13.1 | 11.6 | 345.4 |
| MA | 361.6 | 168.5 | 117.4 | 110.5 | 103.6 | 98.7 | 98.7 | 98.7 | 32.9 | 32.9 | 32.9 | 1,256.4 |
| ME | 8.1 | 2.0 | 1.9 | 1.8 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 25.2 |
| NH | 8.2 | 2.5 | 2.3 | 2.2 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 0.7 | 0.7 | 26.7 |
| RI | 10.9 | 7.3 | 5.4 | 3.7 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 35.5 |
| VT | 36.1 | 20.1 | 13.4 | 7.0 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 1.7 | 117.3 |
| Annual | 498.7 | 246.5 | 179.6 | 178.1 | 149.6 | 144.8 | 123.1 | 123.1 | 57.3 | 56.0 | 49.7 | 1,806.5 |
| Cumulative | 498.7 | 745.2 | 924.8 | 1,102.9 | 1,252.5 | 1,397.3 | 1,520.4 | 1,643.6 | 1,700.9 | 1,756.9 | 1,806.5 | 1,806.5 |
| Estimated Summer Seasonal Claimed Capability (MW, based on 35% of AC nameplate rating and assuming winter SCC equals zero) |  |  |  |  |  |  |  |  |  |  |  |  |
| Annual Summer SCC | 174.5 | 86.3 | 62.9 | 62.3 | 52.4 | 50.7 | 43.1 | 43.1 | 20.1 | 19.6 | 17.4 | 632.3 |
| Cumulative Summer SCC | 174.5 | 260.8 | 323.7 | 386.0 | 438.4 | 489.0 | 532.1 | 575.2 | 595.3 | 614.9 | 632.3 | 632.3 |

The ISO is participating in several DOE projects and conducting independent work to develop a forecast of PV energy production. Projecting PV energy production is exceedingly complex and must account for advanced technical issues, including the anticipated fluctuations of the electric energy output attributable to the weather and the future performance of these resources due to factors such as actual siting characteristics and the reliability of future system components (e.g., inverters, modules). The ISO plans to review and analyze the actual performance of PV resources and other types of data before generating a PV energy forecast. Plans call for continuing discussions on the PV energy forecast with the DGFWG and releasing an ISO forecast in RSP15.

To gain insights into the process for conducting a full PV energy forecast, the ISO analyzed PV’s potential annual energy production for the region using a number of gross assumptions and a weather pattern for 2006. The results showed that a future fleet of 1,800 MW of PV could produce approximately 2,435 GWh in 2023, but the amount of energy production would likely vary because of annual fluctuations of prevailing weather. This estimated annual energy production of approximately 1.6% of the NEL in 2023 is based on the 151,525 GWh net energy for load indicated in Table 3-2 (Section 3.1.1) for that year. Monthly and daily PV energy output will vary more significantly due to weather.

Results of the forecast will inform various ISO system planning functions. For example, the ISO intends to use data from the DG forecast in the following types of analyses:

Transmission needs assessments

Transmission solutions studies

Proposed plan application studies

System impact studies

Economic studies

The ISO will work with stakeholders to explore how to use the DG forecast in the above planning analyses and possibly apply it to other market-related assessments. These may include such tasks as the development of the Installed Capacity Requirement. The ISO will require guidance from FERC on a number of ongoing market changes addressing resource adequacy issues (e.g., the demand curve, capacity zones, and pay for performance) before being able to determine the best methods for potentially incorporating the DG forecast into the resource adequacy process. As part of these processes, the ISO will consider the amounts of PV that participate in the FCM and the wholesale energy markets to ensure that each category is treated in accordance with market rules and that resources are not counted more than once.

### Next Steps

The ISO will consider how to build on the PV forecast, including the potential of additional DG resources, such as combined heat and power resources.

To conduct planning studies at various geographical levels (e.g., state and load zone levels, dispatch zones, and nodes) that account for existing PV resources, the ISO will need to collect data. Specifically, the ISO will need data on the cumulative installed nameplate capacity over time; cumulative energy production; and an accurate breakdown of total PV that participates in the FCM and wholesale energy markets compared with PV that does not participate in the markets (and serves to reduce load). The ISO has begun to work with the region’s distribution utilities to collect this type of data and will continue this effort.

The growth in DG presents some challenges for grid operators and planners. Challenges for the ISO include the following:

A limited amount of data concerning DG resources, including their size, location, and operational characteristics

A current inability to observe and control DG resources in real time

A need to better understand the impacts on system operations of the increasing amounts of DG, including ramping (i.e., rate of starting and stopping), reserve, and regulation requirements

Potential impacts to the reliability of the regional power system posed by future amounts of DG resulting from existing state interconnection standards

The ISO’s work with the DGFWG will help position the region to best integrate rapidly growing DG resources in a way that maintains reliability and allows the states to realize the public policy benefits they have identified as the basis for their DG programs. Section 6.6 discusses other outstanding issues, including DG interconnection requirements and a short-term operations forecast.

## Summary of Key Findings of the Load, Energy-Efficiency, and PV Forecasts

The RSP14 forecasts of annual net energy use and peak loads are key inputs in establishing the system needs discussed in Section 4 through Section 6. The RSP14 forecasts for the annual use of electric energy and summer and winter peak are essentially the same as in RSP13. The key points of the forecast are as follows:

- The forecasts for annual energy use and the summer and winter peaks are not materially different from the RSP13 forecast.

- The ISO will continue examining ways to improve the load forecast and the energy efficiency forecast.

- The gross compound annual growth rate for the ISO’s electric energy use is 1.0% for 2014 through 2023, 1.3% for the summer peak, and 0.6% for the winter peak.

- The annual load forecast minus both the FCM passive demand resources and the ISO EE forecast shows essentially a 0.1% compound annual growth in energy consumption, 0.7% increases in the summer peak load, and 0.1% reductions in the winter peak load.

Through the Distributed Generation Forecast Working Group, the ISO and interested stakeholders have developed a methodology for forecasting New England state policy-supported photovoltaic megawatts and a PV forecast for 2014 to 2023. Ongoing efforts are assessing the potential for broadening the forecast to include other drivers of PV as well as other types of DG resources.

# Resources—Adequacy, Capacity, and Reserves

The ISO’s system planning process identifies the amounts, locations, and types of resources the system needs to ensure resource adequacy and how the region is meeting these needs in the short term through the Forward Capacity Market and the locational Forward Reserve Market (FRM). The amount of capacity the system requires in a given year is determined through the Installed Capacity Requirement calculation, which accounts for uncertainties, contingencies, and resource performance under a wide range of existing and future system conditions. The procurement of operating reserves for the system and local areas address contingencies, such as unplanned outages. Collectively, the forecasts of future electricity demand (as discussed in Section 3), the ICR calculation, the procurement of capacity and reserves, and the operable capacity analyses that consider future scenarios of load forecasts and operating conditions are referred to as the resource adequacy process. Projects proposed through the ISO’s Generator Interconnection Queue, energy-efficiency resources reflected in the ISO’s EE forecast, imports from neighboring systems, and the development of other resources can be used to meet the long-term needs of the system.

This section describes the requirements for resource adequacy over the planning period; the analyses conducted to determine the systemwide and local-area needs for resource adequacy; and the region’s efforts to meet the need for resources through the FCM, the FRM, the queue, and energy-efficiency resources supported by the states. This section also discusses the results of the net operable capacity assessments of the system under a variety of deterministic, stressed-system conditions. The studies and other actions supporting the strategic planning of the region (see Section 6) and other planning coordination, studies, and initiatives (Section 7) are addressing current issues and challenges in meeting short-term and long-term resource needs.

## Determining Systemwide and Local-Area Capacity Needs

The Installed Capacity Requirement forms the basis for determining the systemwide capacity needs. The planning process also determines the need for capacity in local capacity zones, accounting for export and import capabilities (or limitations) of these local zones. The annual Forward Capacity Auctions are intended to procure the needed capacity, systemwide and for capacity zones. The section provides the results of the systemwide and local-area capacity analyses for the planning period.

### Systemwide Installed Capacity Requirements

RSP14 discusses the established ICR values for the 2014/2015 through 2017/2018 capacity commitment periods and illustrates representative net ICR values for the 2019/2020 through 2023/2024 periods. The actual net ICR values for the 2014/2015 through 2017/2018 capacity commitment periods reflect the latest ICR values approved by FERC and are based on the 2013 CELT Report. The representative net ICR values do not indicate the definitive amount of capacity the region will purchase for that period but provide stakeholders with a general forecast of the likely resource needs of the region.

Table 4-1 shows the actual and representative New England net Installed Capacity Requirements for 2014 to 2023. FERC approved the ICR and Hydro-Québec Interconnection Capability Credit (HQICC) values for the 2014/2015 through 2017/2018 commitment periods. The representative net ICR values for 2019/2020 through 2023/2024 are calculated deterministically but are assumed to meet the probabilistic resource adequacy criteria. The table also shows the resulting reserves using the 2014 CELT Report, which are different for every period of the FERC-approved ICR because of assumed changes in tie benefits and other system conditions. In the table, the calculated future net ICR for 2019/2020 to 2023/2024, rounded to the nearest 100 MW, is based on a representative value of 14.2% for resulting reserves for all years. As shown in Table 4-1, the region’s net ICR is expected to grow from 32,588 MW in 2014 to a representative value of 36,100 MW by 2023. This represents a growth of approximately 390 MW per year, which is equivalent to 1.14% per year.

Table 4-1 
Actual and Representative New England Net Installed Capacity Requirements
and Resulting Reserves, 2014 to 2023 (MW, %)

| Years | 2014 CELT Forecast 50/50 Peak (MW) | Actual and Representative Future Net ICR(a) (MW) | Resulting Reserves(b) (%) |
| --- | --- | --- | --- |
| 2014/2015 | 28,165 | 32,588 | 15.7 |
| 2015/2016 | 28,615 | 33,114 | 15.7 |
| 2016/2017 | 29,130 | 33,529 | 15.1 |
| 2017/2018 | 29,610 | 33,855 | 14.3 |
| 2018/2019 | 30,005 | TBD(c) | − |
| 2019/2020 | 30,335 | 34,600 | 14.1 |
| 2020/2021 | 30,675 | 35,000 | 14.1 |
| 2021/2022 | 30,990 | 35,400 | 14.2 |
| 2022/2023 | 31,315 | 35,800 | 14.3 |
| 2023/2024 | 31,620 | 36,100 | 14.2 |

- Net ICR values for 2014/2015 to 2017/2018 are the latest values approved by FERC. These net ICR values were developed using 2013 CELT Report loads.

- The resulting reserves percentage for 2014/2015 to 2017/2018, when calculated using their respective 2013 CELT Report loads, ranged from 13.6% to 15.2% (These values are not shown in the above table). Table 4-1 shows the resulting reserves percentage calculated using the 2014 CELT Report loads. The resulting reserves are 1% to 2% higher than the percentages based on the 2013 CELT loads because the 2013 load forecasts for these years are slightly higher than the 2014 load forecasts.

- In November 2014, the ISO will file with FERC the ICR and net ICR for 2018/2019.

As of the RSP14 publication date, the net ICR for 2018/2019 was under development and scheduled to be filed with FERC in November 2014. In December 2014 or early 2015, the ISO plans to provide the PAC with the representative net ICR values for 2019/2020 through 2023/2024 using the same probabilistic calculation techniques and assumptions used to determine the 2018/2019 net ICR values.

### Local Resource Requirements and Limits

While the ICR addresses New England’s total capacity requirement assuming the system overall has no transmission constraints, certain subareas are limited in their ability to export or import power. To address the impacts of these constraints on subarea reliability, before each FCA, the ISO determines the local sourcing requirement (LSR) and maximum capacity limit (MCL) for certain subareas within New England. An LSR is the minimum amount of capacity that must be electrically located within an import-constrained load zone to meet the ICR. An MCL is the maximum amount of capacity that can be procured in an export-constrained load zone to meet the total ICR for the New England region. Areas that have either an LSR or an MCL and that meet other tests in the market are designated in the Forward Capacity Auction as capacity zones. These designations help ensure that the appropriate amount of capacity is procured within these capacity zones to satisfy the ICR and contribute effectively to total system reliability. (See Section 4.1.3.2 and 4.2 for further discussion of capacity zones.)

The LSR and MCL values, associated with the respective capacity commitment period’s FCA, are included in Table 4-2 for the 2014/2015 through the 2017/2018 capacity commitment periods. Like the net ICR, the LSR and MCL capacity zones and values for FCA #9 were under development at the time of the RSP14 publication and will be filed with FERC in November 2014. In December 2014 or early 2015, the ISO plans to present to the PAC the representative LSR and MCL values for 2019/2020 through 2023/2024 using the same probabilistic calculation techniques and assumptions used for determining the 2018/2019 LSR and MCL values.

Table 4-2
Actual LSRs and MCLs for the 2014/2015 to 2017/2018
Capacity Commitment Periods(a)

| Capacity Commitment Period |  | LSR (MW) |  | MCL (MW) |
| --- | --- | --- | --- | --- |
|  |  | CT | NEMA/Boston | Maine |
| 2014/2015 | FCA #5 | 6,682 | 3,120 | 3,614 |
| 2015/2016 | FCA #6 | 6,806 | 3,238 | 4,139 |
| 2016/2017 | FCA #7 | 6,990 | 3,342 | 4,164 |
| 2017/2018 | FCA #8 | 7,319 | 3,428 | 3,960 |

(a) 	Source: “Summary of ICR, LSR, and MCL for FCM and the Transition Period,” table, in Summary of Historical ICR Values spreadsheet (November 20, 2013), http://www.iso-ne.com/static-assets/documents/markets/othrmkts_data/fcm/doc/summary_of_icr_values_expanded.xls. These are the latest values filed with FERC.

### Capacity Supply Obligations from the Forward Capacity Auctions

This section presents the results of the first eight Forward Capacity Auctions, including the amount of capacity that generation, import, and demand resources in the region will supply.

#### Capacity Supply Obligations for the First Eight FCAs

Table 4-3 shows the results of the eight FCAs held so far for 2010/2011 through 2017/2018 and provides the capacity supply obligation (CSO) totals procured for FCA #1 thru FCA #8 at the conclusion of each auction. This table also includes some details on the types of CSOs procured, including the total real-time emergency generation (see Section 2.4), self-supply obligation values that reflect bilateral capacity arrangements, and import capacity supply obligations from neighboring balancing authority areas.

Table 4-3
Summary of the FCA Obligations at the Conclusion of Each Auction (MW)(a)

| Commitment Period | ICR | HQICC | Net ICR(b) | Capacity Supply Obligation | RTEG Capacity Supply Obligation | RTEG Utilization Ratio | Self-Supply Obligation | Import Capacity Supply Obligation |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 2010/2011 | 33,705 | 1,400 | 32,305 | 34,077 | 875 | 0.686 | 1,593 | 934 |
| 2011/2012 | 33,439 | 911 | 32,528 | 37,283 | 759 | 0.791 | 1,696 | 2,298 |
| 2012/2013 | 32,879 | 914 | 31,965 | 36,996 | 630 | 0.952 | 1,935 | 1,900 |
| 2013/2014 | 33,043 | 916 | 32,127 | 37,501 | 688 | 0.872 | 2.698 | 1,993 |
| 2014/2015 | 34,154 | 954 | 33,200 | 36,918 | 722 | 0.831 | 3,176 | 2,011 |
| 2015/2016 | 34,498 | 1,042 | 33,456 | 36,309 | 617 | 0.972 | 4,164 | 1,924 |
| 2016/2017 | 34,023 | 1,055 | 32,968 | 36,220 | 262 | 1.000 | 4,662 | 1,830 |
| 2017/2018 | 34,923 | 1,068 | 33,855(c) | 33,702(d) | 270 | 1.000 | 3,330 | 1,237 |

  - Information regarding the results of annual reconfiguration auctions is available at http://www.iso-ne.com/markets/othrmkts_data/fcm/cal_results/index.html.

  - The net ICR equals the ICR minus the Hydro-Québec Interconnection Capability Credits. The ICR applies to the FCA, not the reconfiguration auction.

  - The ICR requirement for 2017/2018 will be met by procuring additional resources, if deemed necessary, in annual reconfiguration auctions, in accordance with the market rules.

  - Subsequent to the end of FCA #8 but before the ISO filed the results with FERC, an out-of-market resource from FCA #6 was deemed to have cleared and was assigned a 10 MW capacity supply obligation, increasing the total capacity supply obligation to 33,712 MW.

#### FCA Results for Capacity Zones

Table 4-4 summarizes the detailed CSOs for the capacity zones modeled for each capacity commitment period, which are published in the 2014 CELT Report. The CSOs have been adjusted to reflect the 600 MW limit in the market rule for real-time emergency generation resources, which is the maximum quantity of this resource type that can be counted toward the ICR.

Table 4-4
Results of the FCA by Capacity Zone at the Conclusion of Each Auction (MW, $/kW-month)(a)

| Commitment Period | Modeled Capacity Zone | MCL | LSR | CSO | RTEG CSO | Self-Supply Obligation | Capacity Clearing Price | Payment Rate | RTEG Payment Rate |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | (MW) |  |  |  |  | ($/kW-month) |  |  |
| 2010/2011 | Rest-of-Pool |  |  | 30,572 | 838 | 1,584 | 4.500 | 4.254 | 2.918 |
|  | Maine | 3,855 |  | 3,505 | 37 | 9 | 4.500 | 4.254 | 2.918 |
| 2011/2012 | Rest-of-Pool |  |  | 33,468 | 727 | 1,687 | 3.600 | 3.119 | 2.467 |
|  | Maine | 3,395 |  | 3,815 | 32 | 9 | 3.600 | 3.119 | 2.467 |
| 2012/2013 | Rest-of-Pool |  |  | 33,099 | 597 | 1,925 | 2.951 | 2.535 | 2.413 |
|  | Maine | 3,275 |  | 3,897 | 33 | 9 | 2.951 | 2.465 | 2.347 |
| 2013/2014 | Rest-of-Pool |  |  | 33,476 | 655 | 2,693 | 2.951 | 2.516 | 2.194 |
|  | Maine | 3,187 |  | 4,025 | 33 | 6 | 2.951 | 2.336 | 2.036 |
| 2014/2015 | Rest-of-Pool |  |  | 32,960 | 691 | 3,171 | 3.209 | 2.855 | 2.374 |
|  | Maine | 3,702 |  | 3,958 | 31 | 5 | 3.209 | 2.885 | 2.374 |
| 2015/2016 | Rest-of-Pool |  |  | 32,374 | 582 | 4,157 | 3.434 | 3.129 | 3.044 |
|  | Maine | 3,888 |  | 3,935 | 35 | 7 | 3.434 | 3.129 | 3.044 |
| 2016/2017 | Rest-of-Pool |  |  | 20,182 | 80 | 4076 | 3.150 | 2.744 | 2.744 |
|  | Maine | 3,709 |  | 3,950 | 12 | 26 | 3.150 | 2.744 | 2.744 |
|  | Connecticut |  | 7,603 | 8,372 | 143 | 499 | 3.150 | 2.883 | 2.883 |
|  | NEMA/Boston(b) |  | 3,209 | 3,716 | 28 | 61 | 14.999 | New: 14.999 Existing: 6.661 | 6.661 |
| 2017/2018 | Rest-of-Pool |  |  | 15,901 |  | 2,238 | New: 15.000 Existing: 7.025 | N/A | 7.025 |
|  | Maine | 3,960 |  | 3,553 | 12 | 14 | New: 15.000 Existing: 7.025 | N/A | 7.025 |
|  | Connecticut |  | 7,319 | 9,191 | 138 | 1,017 | New: 15.000 Existing: 7.025 | N/A | 7.025 |
|  | NEMA/Boston(c) |  | 3,428 | 3,821 | 26 | 61 | 15.000 | N/A | 15.000 |

    - Values are rounded and do not reflect proration.

    - Insufficient competition triggered in NEMA/Boston for 2016/2017.

    - The Capacity Carry Forward Rule was triggered in NEMA/Boston. This rule addresses situations where a large resource meets a zonal need but eliminates any need for new resources in the subsequent auction (Market Rule 1, Section III.13.2.7.9).

Two capacity zones, Maine and the Rest-of-Pool, were used in FCA #1 through FCA #6 to address Maine’s designation as an export-constrained capacity zone. The potential import-constrained capacity zones were determined to have sufficient existing capacity to meet the local-sourcing requirements for FCA #1 through FCA #6. In its March 30, 2012, order on tariff revisions to the FCM, FERC accepted the ISO’s proposal to model four capacity zones for FCA #7. These capacity zones were Maine, which was designated as an export-constrained capacity zone; NEMA/Boston and Connecticut, which were designated as import-constrained capacity zones; and the Rest-of-Pool, which combined the other four capacity zones. FCA #8 used the same four capacity zones as FCA #7.

For FCA #8, the ISO submitted a filing to FERC proposing to continue to model the same four zones used in FCA #7 but then initiating a stakeholder process to develop a zonal structure for the market that better reflects reliability needs of the system. After the ISO provided FERC with additional requested information, FERC accepted the use of the existing four capacity zones and is requiring the ISO to pursue the stakeholder process for determining future zones as originally proposed (see Section 4.2). This process was initiated over the summer 2013 and will develop criterion and processes for creating, modifying, or collapsing capacity zones, as appropriate. (Section 4.2 contains additional information on FCM capacity zones.)

After FCA #8, available capacity resources in the Connecticut capacity zone exceeded the resource adequacy requirements for the area by 1,872 MW. This is an increase of approximately 1,100 MW over the FCA #7 excess of 769 MW. In this zone for the 2017/2018 capacity commitment period, 9,191 MW of capacity resources will be used to meet the local sourcing requirement of 7,319 MW. An additional 100 MW of capacity also was procured in Connecticut to support an administrative export delist bid through that capacity zone.

In the NEMA/Boston capacity zone, the Capacity Carry Forward Rule was triggered because a new resource that cleared in FCA #7 precluded the need for new resources in the subsequent auction. The intent of the Carry Forward Rule is to reset the clearing price administratively when new additional capacity would have been needed and consequently would have set the clearing price, but did not, because of an excess amount of additional new capacity procured in the prior auction. Table 4-5 shows, by resource type, the amounts of new capacity procured during all the FCAs.

Table 4-5
Capacity Supply Obligation for New Capacity
Procured during the Forward Capacity Auctions (MW)(a)

| Capacity Resource | FCA #1 | FCA #2 | FCA #3 | FCA #4 | FCA #5 | FCA #6 | FCA #7 | FCA #8 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Generation resources | 40 | 1,157 | 199 | 114 | 42 | 79 | 800 | 27 |
| Demand-resource total | 860 | 447 | 309 | 515 | 263 | 313 | 245 | 355 |
| Active demand resources | 576 | 185 | 98 | 257 | 42 | 66 | <1 | 14 |
| Passive demand resources | 284 | 262 | 211 | 258 | 221 | 247 | 245 | 341 |
| Import resources | 0 | 1,529 | 817 | 831 | 871 | 1,648 | 1,718 | 1,154 |

(a) 	New RTEG capacity is not included in the table values because the FCA treats it as existing capacity. Repowered existing generating capacity (i.e., capacity that has undergone environmental upgrades), which is treated as new capacity in the FCA, has been removed as well. Refer to the full auction results at http://www.iso-ne.com/isoexpress/web/reports/auctions/-/tree/fcm-auction-results.

#### Outcomes of 2013 Delist Bids

In the first seven capacity auctions held since 2008, with one limited exception, the market cleared at the price floor, and the region procured a significant excess of capacity. As recently as fall 2013, a surplus of capacity resources (both new and existing) appeared likely to be participating in the eighth FCA.

After the deadline for seeking to qualify new resources to participate in the eighth FCA, however, the capacity supply situation in New England changed dramatically. In August 2013, Entergy announced the retirement of the Vermont Yankee (VY) nuclear plant (604 MW) and submitted a nonprice retirement request (NPRR). The ISO subsequently determined the resource was not needed for reliability. In late September/early October 2013, other market participants submitted NPRRs for an additional 2,531 MW to leave the market. This total consisted of five resources representing 1,535 MW from the Brayton Point Station, three resources representing 342 MW from Norwalk Harbor Station, 100 MW from several small generating resources, and approximately 554 MW of demand resources.

On December 20, 2013, the ISO issued the reliability determination for these resources stating that the Brayton Point Station generators #1 to #4 were needed for reliability. Given Brayton Point’s subsequent decision to retire on June 1, 2017, these events combined to change the supply-demand balance from a surplus of over 2,000 MW of existing resources to a deficiency of over 1,000 MW compared with the ICR. This abrupt change in the supply-demand balance, coupled with a general decline in the amount of new resources seeking to participate in the auction (see Table 4-5), resulted in insufficient competition among new resources for setting a competitive price in the auction and thus prices being set by administrative pricing rules in the tariff.

#### Representative Systemwide Resource Needs

The systemwide capacity needs are shown by the representative net ICR values for future years (see Section 4.1.1). Table 4-6 compares these systemwide needs with the resources procured in FCA #8, accounting for the energy-efficiency forecast (see Section 3.2) that projects the future levels of passive demand resources. This projection assumes that all resources with capacity supply obligations through FCA #8 are in commercial service by the start of the eighth capacity commitment period commencing in June 2017 and that they remain in service for the 10-year planning horizon. The resource shortages from 2019 through 2023 respectively show the minimum amount of regional system needs, assuming that no additional retirements occur. As shown in Table 4-6, the region is expected to need approximately 425 MW of new resources starting with 2019, and the cumulative need is expected to increase to approximately 1,155 MW, if the projected load and capacity assumptions materialize.

Table 4-6 
Future Systemwide Needs (MW)

| Year | 50/50 Peak Load | Representative Net ICR (Need) | FCA #8 (Known Resources)(a) | EE Forecast (New Resource)(b) | Resource Surplus/Shortage(c) |
| --- | --- | --- | --- | --- | --- |
| 2019/2020 | 30,335 | 34,600 | 33,712 | 464 | −424 |
| 2020/2021 | 30,675 | 35,000 | 33,712 | 675 | −613 |
| 2021/2022 | 30,990 | 35,400 | 33,712 | 873 | −815 |
| 2022/2023 | 31,315 | 35,800 | 33,712 | 1,059 | −1,029 |
| 2023/2024 | 31,620 | 36,100 | 33,712 | 1,233 | −1,155 |

(a)	FCA #8 resource numbers are based on FCA #8 auction results, assuming no retirements and the same level of imports (i.e., most imports need to requalify for every auction). Details are available at http://www.iso-ne.com/regulatory/ferc/filings/2014/feb/er14_1409-000_fca8_results_filing_2-28-2014.pdf.

(b) 	EE forecast values are based on the 2014 EE forecast. Details are available at http://www.iso-ne.com/committees/comm_wkgrps/othr/enrgy_effncy_frcst/2014mtrls/iso_ne_draft_final_2014_ee_forecast_2018_2023.pdf.

(c) 	Additional resources would be required if additional resources retired or fewer resources were imported from neighboring regions.

## FCM Capacity Zones

Beginning with FCA #9, several tariff changes became effective that require a new methodology for determining the appropriate number of capacity zones to model in the Forward Capacity Market and the appropriate boundaries for these capacity zones. Under the changes, the ISO will annually identify and evaluate all the boundaries and interface transfer capabilities that could be relevant to FCA capacity zone modeling. This review will not be limited to existing energy load zone or capacity zone boundaries. Instead, it must focus on the actual constraints observed and expected on the New England system and directly consider submitted retirements and rejected delist bids to thus be responsive to these and other system changes. The capacity zones will be used in primary auctions, reconfiguration auctions, and FCM settlements.

The new FERC-approved methodology for determining capacity zones is a two-step process. Step one identifies potential zonal boundaries and associated transfer limits to be tested for modeling in the auction. Step two uses objective criteria to determine whether or not a zone should be modeled for the pertinent capacity commitment period. With respect to step two, the trigger to model an import-constrained zone is based on the quantity of existing resources in the zone, whereas the trigger to model an export-constrained zone is based on the quantity of existing and proposed new resources in the zone. Zones that are neither import- or export-constrained are collapsed into the Rest-of-Pool capacity zone.

This section of the RSP describes the outcomes of the first step of the methodology, namely, the identification of potential zonal boundaries and associated transfer limits to be tested for modeling in the FCM. In particular, the results of the annual assessment of transmission transfer capability are presented. The assessment was conducted pursuant to applicable NERC, NPCC, and ISO New England standards and criteria and identified the portions of the system with potential future transmission system weaknesses and limiting facilities that could affect the transmission system’s ability to reliably transfer energy in the planning horizon.

The transfer capability analysis of the New England system incorporated the results of several recent studies. In some cases, the transfer limits were based on equipment thermal limitations during summer peak conditions. In other cases, voltage or transient stability limitations were identified at off-peak load levels. All the analyses included all transmission upgrades that had been certified and accepted to be in service in time for the ninth capacity commitment period (i.e., by June 1, 2018). The interstate portions of the New England East–West solution (see Section 5.3 and 5.4) were included among the certified and accepted upgrades. The transfer capability assessment also modeled the recent nonprice retirements of the Vermont Yankee Nuclear Facility, the Norwalk Harbor Station, and the Brayton Point station (see Sections 4.1.3.3, 5.4.2.2, and 5.7). Table 4-7 shows the transfer capabilities identified for multiple interfaces for all years on the RSP planning horizon.

Table 4-7
Results of the Transfer Capability Analysis for New England, 2014 to 2023 (MW)

| Interface(a) | Year |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 |
| New Brunswick–New England(b) | 700 | 700 | 700 | 700 | 700 | 700 | 700 | 700 | 700 | 700 |
| Orrington South Export | 1,200 | 1,325(c) | 1,325 | 1,325 | 1,325 | 1,325 | 1,325 | 1,325 | 1,325 | 1,325 |
| Surowiec South | 1,150 | 1,500(c) | 1,500 | 1,500 | 1,500 | 1,500 | 1,500 | 1,500 | 1,500 | 1,500 |
| Maine–New Hampshire | 1,600 | 1,900(c) | 1,900 | 1,900 | 1,900 | 1,900 | 1,900 | 1,900 | 1,900 | 1,900 |
| North-South | 2,700 | 2,700 | 2,700 | 2,700 | 2,700 | 2,700 | 2,700 | 2,700 | 2,700 | 2,700 |
| East–West | 2,800 | 2,800 | 2,800 | 2,800 | 3,500(d) | 3,500 | 3,500 | 3,500 | 3,500 | 3,500 |
| West–East | 1,000 | 1,000 | 1,000 | 1,000 | 2,200(d) | 2,200 | 2,200 | 2,200 | 2,200 | 2,200 |
| Boston Import (N-1) | 4,850(e) | 4,850 | 4,850(f) | 4,850 | 4,850 | 4,850 | 4,850 | 4,850 | 4,850 | 4,850 |
| Boston Import (N-1-1) | 4,175(e) | 4,175 | 4,175(f) | 4,175 | 4,175 | 4,175 | 4,175 | 4,175 | 4,175 | 4,175 |
| SEMA/RI Export | 3,000 | 3,000 | 3,000 | 3,000 | 3,400(d) | 3,400 | 3,400 | 3,400 | 3,400 | 3,400 |
| SEMA/RI Import (N-1) | - | - | - | - | 786 | 786 | 786 | 786 | 786 | 786 |
| SEMA/RI Import (N-1-1) | - | - | - | - | 473 | 473 | 473 | 473 | 473 | 473 |
| Connecticut Import (N-1) | 3,050 | 3,050 | 2,800(d) | 2,800 | 2,950 | 2,950 | 2,950 | 2,950 | 2,950 | 2,950 |
| Connecticut Import (N-1-1) | 1,850 | 1,850 | 1,600(d) | 1,600 | 1,750 | 1,750 | 1,750 | 1,750 | 1,750 | 1,750 |
| SW Connecticut Import (N-1) | 3,200 | 3,200 | 3,200 | 3,200 | 3,200 | 3,200 | 3,200 | 3,200 | 3,200 | 3,200 |
| SW Connecticut Import (N-1-1) | 2,300 | 2,300 | 2,300 | 2,300 | 2,300 | 2,300 | 2,300 | 2,300 | 2,300 | 2,300 |
| HQ-NE (Highgate) | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 |
| HQ-NE (Phase II)(g) | 1,400 | 1,400 | 1,400 | 1,400 | 1,400 | 1,400 | 1,400 | 1,400 | 1,400 | 1,400 |
| Cross–Sound Cable (CSC) (In)(h) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |
| Cross–Sound Cable (CSC) (Out) | 346 | 346 | 346 | 346 | 346 | 346 | 346 | 346 | 346 | 346 |
| NY-NE Summer(i) | 1,400 | 1,400 | 1,400 | 1,400 | 1,400 | 1,400 | 1,400 | 1,400 | 1,400 | 1,400 |
| NY-NE Winter(i) | 1,875 | 1,875 | 1,875 | 1,875 | 1,875 | 1,875 | 1,875 | 1,875 | 1,875 | 1,875 |
| NE-NY Summer(i) | 1,200 | 1,200 | 1,200 | 1,200 | 1,200 | 1,200 | 1,200 | 1,200 | 1,200 | 1,200 |
| NE-NY Winter(i) | 1,400 | 1,400 | 1,400 | 1,400 | 1,400 | 1,400 | 1,400 | 1,400 | 1,400 | 1,400 |

(a) The transmission interface limits are single-value, summer peak (except where noted to be winter), for use in subarea transportation models. The limits may not include possible simultaneous impacts and should not be considered as “firm.” (The bases for these limits will be subject to more detailed review.) For the years within the FCM horizon (2018, FCA #9 and sooner), only accepted certified transmission projects are included when identifying transfer limits. Certified transmission projects were presented to the Reliability Committee at their January 21, 2014, meeting (http://www.iso-ne.com/committees/reliability/reliability-committee). For the years beyond the FCM horizon (2019 and later), proposed plan approved transmission upgrades are included according to their expected in-service dates.
(b) The electrical limit of the New Brunswick–New England (NB–NE) tie is 1,000 MW. When adjusted for the ability to deliver capacity to the ISO New England Balancing Authority Area, the NB–NE transfer capability is 700 MW because of downstream constraints, in particular, Orrington South.
(c) The relevant in-service date for the Maine Power Reliability Program is 2015.

(d) The PTOs have certified that the NEEWS Interstate Reliability Project (IRP) project would be in service by December 2015 and have listed this as the project’s in-service date in the RSP Project List. The ISO has accepted the PTO’s certification of the IRP project for FCA #8, and has accepted—for the purpose of conducting the calculations described in Section 4—that the project will be in service by June 1, 2017, although it may be in service before that date. The Lake Road generating facility will be modeled in the Connecticut capacity zone for 2017/2018 capacity commitment period. The ISO has not yet determined whether the Lake Road generating facility can be modeled in this zone for an earlier CCP.
(e) The Boston import capabilities change in 2014 as a result of the retirement of Salem Harbor combined with the inclusion of the advanced NEMA/Boston upgrades.
(f) The effect of the addition of the Footprint generation project on the Boston import capability will be evaluated at a future date.

(g) The HQICC interconnection is a DC tie with equipment ratings of 2,000 MW. The PJM and NYISO systems may be constrained by the loss of this line. As a result, ISO New England has assumed that its transfer capability is 1,400 MW for capacity and reliability calculations. This assumption is based on the results of loss-of-source analyses conducted by PJM and NYISO.
(h) The import capability on the CSC is dependent on the level of local generation.
(i) The New York interface limits are without the CSC and with the Northport–Norwalk Cable at 0 MW flow. Simultaneously importing into New England and SWCT or CT can lower the NY–NE capability (very rough decrease = 200 MW). Conversely, simultaneously exporting to NY and importing to SWCT or CT can lower the NE–NY capability (very rough decrease = 700 MW).

The existing eight energy load zones were surveyed to identify whether modeling these zones as FCM capacity zones would be appropriate. The load and resource conditions in each zone were analyzed, and the second-contingency transmission-performance characteristics of the zones were considered.

As a result of the above reviews, the ISO proposed to evaluate for FCA #9 three potential import-constrained capacity zones using the objective criteria modeling triggers put forth in the tariff. The three potential import-constrained zones are Connecticut, NEMA/Boston, and a combined Southeast Massachusetts/Rhode Island zone. Testing the Maine load zone as an export-constrained zone was proposed. Any energy load zone that does not exceed the automatic modeling trigger will be collapsed into the Rest-of-Pool capacity zone.

## Determining Operating Reserves and Regulation

In addition to capacity resources being available to meet the region’s actual demand for electricity, as discussed in Section 4.1, the system needs a certain amount of resources that can provide operating reserves and system regulation. The overall mix of resources providing operating reserves must be able to respond quickly to system contingencies stemming from equipment outages. The ISO may also call on these resources to provide regulation service for maintaining system frequency and external transactions with neighboring balancing authority areas or to serve load during peak demand conditions. A suboptimal mix of resources overall, with limited amounts of flexible operating characteristics, could result in the system’s dependence on more costly resources to provide these services. In the worst case, reliability would be degraded.

Several types of resources in New England have the operating characteristics to respond to contingencies, provide regulation service, and serve peak demand. The generating units that provide operating reserves can respond to contingencies within 10 or 30 minutes and can either be synchronized or not synchronized to the power system. Synchronized (i.e., spinning) operating reserves are on-line resources that can increase output. Nonsynchronized (i.e., nonspinning) operating reserves are off-line, fast-start resources that can be electrically synchronized to the system quickly, reaching maximum output within 10 minutes or within 30 minutes. During real-time daily operations, the ISO determines operating-reserve requirements for the system as a whole and for major import-constrained areas.

This section discusses the need for operating reserves, both systemwide and in major import areas, and the use of specific types of fast-start resources to fill these needs. An overview of the Forward Reserve Market and a forecast of representative future operating-reserve requirements for Greater Southwest Connecticut, Greater Connecticut, and BOSTON are provided. This section also discusses the likely need for additional flexible resources identified by the studies and other actions supporting the strategic planning of the region, as discussed in Section 6.

### Systemwide Operating-Reserve Requirements

The ISO’s operating-reserve requirements, as established in Operating Procedure No. 8, Operating Reserve and Regulation (OP 8), are used to protect the system from the impacts associated with a loss of generating or transmission equipment within New England. A certain amount of the power system’s resources must be available to provide operating reserves to assist in addressing systemwide contingencies.

To comply with OP 8, the ISO must maintain sufficient reserves in its balancing authority area during normal conditions to be able to replace within 10 minutes the first-contingency loss (N−1) in the New England Reliability Control Area/Balancing Authority Area multiplied by the contingency-reserve adjustment (CRA) factor for the most recent completed quarter. The current total 10-minute operating-reserve requirement reflecting the CRA factor is 1.25% of the first-contingency loss. In addition, OP 8 requires the ISO to maintain sufficient reserves to address the uncertainties associated with resource nonperformance, as well as load forecast error and gas-fuel dependence. To meet this requirement, the ISO must be able to replace at least 50% of the next-largest contingency loss (N−1−1) within 30 minutes plus a replacement reserve requirement of 180 MW during Eastern Standard Time and 160 MW during Daylight Savings Time. The higher amount set for the winter period is to accommodate the additional peak-load ramping and fuel uncertainty usually experienced during this period.

Typically, the largest first-contingency loss is between 1,300 and 1,700 MW, and 50% of the next-largest contingency loss is between 600 and 750 MW. These resources typically consist of some combination of the two largest on-line generating units or imports on the Phase II interconnection with Québec.

In accordance with NERC and NPCC criteria for power system operation, ISO Operating Procedure No. 19 (OP 19), Transmission Operations, requires system power flows to stay within applicable emergency limits of the power system elements that remain after the loss of any other power system element (N−1). This N−1 limit may be a thermal, voltage, or stability limit of the transmission system. OP 19 further stipulates that within 30 minutes of the loss of the first-contingency element, the system must be able to return to a normal state that can withstand a second contingency. To implement these OP 19 requirements, and as set forth in OP 8, operating reserves must be distributed throughout the system. This requirement is designed to ensure that the ISO can activate all reserves without exceeding transmission system limitations and that the operation of the system remains in accordance with NERC, NPCC, and ISO New England criteria and guidelines.

### Locational Forward Reserve Market Requirements for Major Import Areas

To maintain system reliability further, the ISO must maintain certain reserve levels within major importing subareas of the system that rely on imports of power from outside the subarea. The amount and type of operating reserves required within these “load pockets” depend on many factors, including load levels, the projected peak load of the subarea, and the operating characteristics of the generating units within the subarea. The systemwide commitment and economic dispatch of generation, system topology, system reliability constraints, special operational considerations, possible resource outages, and other system conditions are additional factors that can affect required levels of reserve within subareas.

The ISO analyzes and determines how the generating resources within the load pockets must be committed to meet the following day’s operational requirements and withstand possible contingencies, including the most critical contingencies that determine the transmission import capability into the subarea. If maximizing the use of transmission import capability to meet demand is more economical, the subarea will require more local operating reserves to protect for contingencies. If using import capability to meet demand is less economical, generation located outside the subarea could provide operating reserves, thus reducing operating-reserve support needed within the subarea. The locational Forward Reserve Market is in place to procure these required operating reserves.

Table 4-8 shows representative future operating-reserve requirements for Greater Southwest Connecticut, Greater Connecticut, and BOSTON. These estimated requirements are based on the same methodology used to calculate the requirements for the locational FRM. The estimates account for representative future system conditions for load, economic generation, generation availability, N−1 and N−1−1 transfer limits, and normal criteria contingencies for generation and transmission in each subarea. The analysis accounts for transmission upgrades consistent with Table 4-7 (in Section 4-2). The representative values show a range to reflect the load and resource uncertainties associated with future system conditions. Table 4-8 also shows the existing amount of fast-start capability located in each subarea resulting from the fast-start resource offered into past FRM auctions. The total 10-minute operating reserve values associated with the FRM reflect the contingency reserve adjustment, but this adjustment does not affect the amount of reserves distributed to locations (i.e., the reserve values for BOSTON, SWCT, and Greater CT did not increase).

Table 4-8 
Representative Future Operating-Reserve Requirements in Major New England Import Areas (MW)

| Area/Improvement | Market Period(a) | Range of Fast-Start Resources Offered into the Past Forward Reserve Auctions (MW)(b) | Representative Future Locational Forward Reserve Market Requirements (MW) |  |
| --- | --- | --- | --- | --- |
|  |  |  | Summer(c) (Jun to Sep) | Winter(c) (Oct to May) |
| Greater Southwest Connecticut(d) | 2014 | 199–515 | 94(e) | To be determined(e) |
|  | 2015 |  | 0–200 | 0–250 |
|  | 2016 |  | 0–225 | 0–300 |
|  | 2017 |  | 0–250 | 0–325 |
|  | 2018 |  | 0–300 | 0–350 |
| Greater Connecticut(f, g) Interstate Reliability Project (IRP) of the New England East–West Solution (NEEWS)(f) | 2014 | 659–1,563(h) | 900(e) | To be determined(e) |
|  | 2015 |  | 400–1,000 | 0–500 |
|  | 2016 |  | 500–1,100 | 0–500 |
|  | 2017 |  | 150–700 | 0–300 |
|  | 2018 |  | 100–700 | 0–200 |
| BOSTON(g, i) | 2014 | 0–441 | 0(e) | To be determined(e) |
|  | 2015 |  | 0–200 | 0–300 |
|  | 2016 |  | 0–250 | 0–300 |
|  | 2017 |  | 0–350 0, if Footprint is in service | 0–350 0, if Footprint is in service |
|  | 2018 |  | 0–350 0, if Footprint is in service | 0–250 0, if Footprint is in service |

- The market period is from June 1 through May 31 of the following year.

- These values are the range of the megawatts of resources offered into the past forward-reserve auctions. The amount offered into the auctions for BOSTON decreased in recent years as the reserve requirements for the market decreased. A summary of the forward-reserve offers for the past auctions is available at http://www.iso-ne.com/isoexpress/web/reports/auctions/-/tree/fwd-rsv-auc-offer.

- “Summer” means June through September of a capability year; “winter” means October of the associated year through May of the following year (e.g., the 2014 winter values are for October 2014 through May 2015). The representative values show a range to reflect uncertainties associated with the future system conditions.

- The assumed N−1 and N−1−1 values to reflect transmission import limits into Greater Southwest Connecticut are 3,200 MW and 2,300 MW, respectively.

- These values are actual locational forward-reserve requirements. The projections of the requirements for future years are based on assumed contingencies.

- For Greater Connecticut, the assumed import limits reflect an N−1 value of 3,050 MW and an N−1−1 value of 1,850 MW through 2016 after the in-service of Greater Springfield Reliability Project (GSRP) in 2013. With the Card–Lake Road line assumed in service in 2017, the definition of the import interface will change, so that the assumed Greater Connecticut N−1 and N−1−1 import limits will be 2,800 MW and 1,600 MW respectively, increasing to 2,950 MW and 1,750 MW, respectively, starting in 2018. The PTOs have certified that the IRP project would be in service by December 2015 and have listed this as the project’s in-service date in the RSP Project List. The ISO has accepted the PTO’s certification of the IRP project for FCA #8, and has accepted—for the purpose of conducting the calculations described in Section 4—that the project will be in service by June 1, 2017, although it may be in service before that date.

- In some circumstances when transmission contingencies are more severe than generation contingencies, shedding some nonconsequential load (i.e., load shed that is not the direct result of the contingency) may be acceptable.

- These values include resources in Greater Southwest Connecticut.

- The assumed N−1 and N−1−1 values reflecting transmission import limits into BOSTON are 4,850 MW and 4,175 MW, respectively reflect the impacts of the retirement of Salem Harbor units #1–#4 and the North Shore Upgrade. The operating-reserve values for BOSTON would be lower with transmission upgrades or without the consideration of the common-mode failure of Mystic units #8 and #9, which are assumed would trip (up to 1,400 MW) because of a failure of the units’ common fuel supply. The 2017 values for NEMA/Boston also show the forward-reserve requirement, assuming that Footprint Power, 674 MW, will be in service by June 2016.

Because the local contingency requirements in Greater SWCT are nested within CT (i.e., operating reserves meeting the Greater SWCT requirement also meet the Greater Connecticut requirement), resources installed in the Greater SWCT area also would satisfy the need for resources located anywhere in Greater Connecticut.

#### Greater Southwest Connecticut

As shown in Table 4-8, Greater SWCT is expected to require as much as 350 MW of operating reserves in the area during the study period. Consistent with ISO’s operating experience of recent years, the interface into Greater Southwest Connecticut is expected to be heavily loaded because of economical transfers into the area. As a result of the heavy loading of the interface capability, more reserves must be carried locally within Greater SWCT.

#### Greater Connecticut

Past RSPs and market signals had identified the need for in-merit and fast-start resources in Greater Connecticut to meet reliability requirements and reduce out-of-merit market costs. As a result of resource development, Greater Connecticut is now projected to have adequate fast-start resources, and the economic performance of this area is expected to improve. As much as 1,563 MW of fast-start resources were offered into the past summer auctions for Greater Connecticut. For 2014, approximately 1,120 MW of fast-start resources were offered into the locational Forward Reserve Market, which exceeds the 900 MW of the reserve requirement established by the FRM for summer 2014. The analysis assumed that the NEEWS Interstate Reliability Project would be in service by 2017 (see Section 5.4.2). This project would both increase system transfer capabilities and result in the Lake Road generating plant being electrically within Greater Connecticut. These changes would allow the ISO more flexibility in achieving the most economical energy production while maintaining an adequate amount of operating reserves for Greater Connecticut.

#### BOSTON

The FRM requirements for the BOSTON subarea shown in Table 4-8 reflect the possible simultaneous contingency loss of Mystic units #8 and #9. The retirement of the Salem Harbor units in 2014 reduces the ability to serve load economically within the BOSTON subarea, which increases the reserve requirements. However, both the North Shore transmission upgrades (that increases the transmission transfer capabilities into BOSTON) and the planned addition of Footprint Power (that increases local generation in the area) more than offset the effects of the reduced amount of Salem Harbor generation available to serve the BOSTON subarea loads. (Refer to Table 4-8, note i.)

If the transmission lines were fully utilized to import lower-cost generation into BOSTON, this subarea would need to provide operating reserves to protect against the larger of (1) the loss of the largest generation source within the subarea and a transmission line or (2) the loss of two transmission lines into the subarea. As much as 441 MW of fast-start resources were offered into the past FRM auctions. The expected amount of existing fast-start resources located in BOSTON will likely meet the estimates of representative local reserve requirements for BOSTON during the study timeframe.

#### Summary of Forward Reserve Market Requirements in Major Load Pockets

New England must meet its overall operating-reserve requirements and have sufficient reserves in load pockets to meet reliability requirements. The need for operating reserves has grown for Greater SWCT, but existing resources will be sufficient to meet this need. The recent additions of fast-start resources in Greater Connecticut provide needed operating flexibility as well as operating reserves. Planned baseload resources (i.e., those assumed to run for long continuous hours at a constant output with little flexibility) also would decrease the amounts of reserves required within the subarea of BOSTON. Existing fast-start resources will likely be adequate to meet the locational reserve requirements for these import areas. Any reduction in traditional baseload resources in either area would increase the locational FRM requirement.

The potential retirement of generating units could affect the need for locational operating reserves and the definition of the zones for operating-reserve requirements.

## Analyzing Operable Capacity

The ISO analyzes the systemwide operable capacity to estimate the net capacity that will be available under two scenarios (i.e., using the 50/50 and 90/10 forecasts of peak load). The analysis identifies operable capacity margins, assuming peak-load conditions and that New England will only have an amount of capacity equal to the net ICR to meet the assumed peak demand plus operating-reserve requirements. A negative margin for a specific scenario indicates the extent that possible mitigation actions would be required through predefined protocols, as prescribed in the ISO’s Operating Procedure No. 4, Action during a Capacity Deficiency, or Operating Procedure No. 7 (OP 7), Action in an Emergency.

Figure 4-1, Table 4-9, and Table 4-10 show the results of the ISO’s systemwide operable capacity analysis for 2014 to 2023. The analysis does not take into account operable capacity needs for RSP subareas. The results show that if the loads associated with the 50/50 forecast occurred, the ISO would expect New England to experience a negative operable capacity margin ranging from 50 MW to 230 MW six out of the 10 years of the study period. The ISO system operators will have to rely on load and capacity relief from OP 4 actions to mitigate the possible capacity shortages.

Figure 4-1: Projected summer operable capacity analysis, 2014 to 2023.

Note: Each year indicates the starting year for the respective capacity commitment period. Total net capacity values for 2014/2015 to 2017/2018 are based on the net ICR filed with FERC. The net capacity for 2019/2020 to 2023/2024 is based on representative net ICR values. The net capacity for 2018/2019 is under development and will be determined after the net ICR for 2018/2019 is filed with FERC in November 2014.

Table 4-9
Projected New England Operable Capacity Analysis for Summer, 2014 to 2023,
Assuming 50/50 Loads (MW)

| Capacity Situation (Summer MW) | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Load (50/50 forecast) | 28,165 | 28,615 | 29,130 | 29,610 | 30,005 | 30,335 | 30,675 | 30,990 | 31,315 | 31,620 |
| Operating reserves(a) | 2,375 | 2,375 | 2,375 | 2,375 | 2,375 | 2,375 | 2,375 | 2,375 | 2,375 | 2,375 |
| Total requirement | 30,540 | 30,990 | 31,505 | 31,985 | 32,380 | 32,710 | 33,050 | 33,365 | 33,690 | 33,995 |
| Installed capacity (net ICR)(b) | 32,588 | 33,114 | 33,529 | 33,855 | N/A | 34,600 | 35,000 | 35,400 | 35,800 | 36,100 |
| Assumed unavailable capacity | −2,100 | −2,100 | −2,100 | −2,100 | −2,100 | −2,100 | −2,100 | −2,100 | −2,100 | −2,100 |
| Total net capacity(c) | 30,488 | 31,014 | 31,429 | 31,755 | N/A | 32,500 | 32,900 | 33,300 | 33,700 | 34,000 |
| Operable capacity margin(d) | −52 | 24 | −76 | −230 | N/A | −210 | −150 | −65 | 10 | 5 |

(a)	The 2,375 MW value of operating reserves is based on the following assumptions: a first contingency of 1,400 MW plus a 25% increase in the 10-minute operating reserve to compensate for nonperformance of the reserve generating units (as discussed in Section 4.3.1) equal to 350 MW, and 30-minute reserves of 625 MW (one half of 1,250 MW).

(b)	Net ICR values for 2014/2015 to 2017/2018 are the latest values approved by FERC. These net ICR values were developed using 2013 CELT Report loads. The ICR values for other years are consistent with the representative future net ICR values in Table 4-1.

(c) 	The net capacity values are equal to the net ICR minus the assumed unavailable capacity.

(d) 	“Operable capacity margin” equals “total net capacity” minus “total requirement.”

Table 4-10
Projected New England Operable Capacity Analysis for Summer, 2014 to 2023,
Assuming 90/10 Loads (MW)

| Capacity Situation (Summer MW) | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Load (90/10 forecast) | 30,470 | 30,950 | 31,495 | 32,005 | 32,430 | 32,790 | 33,160 | 33,505 | 33,865 | 34,195 |
| Operating reserves(a) | 2,375 | 2,375 | 2,375 | 2,375 | 2,375 | 2,375 | 2,375 | 2,375 | 2,375 | 2,375 |
| Total Requirement | 32,845 | 33,325 | 33,870 | 34,380 | 34,805 | 35,165 | 35,535 | 35,880 | 36,240 | 36,570 |
| Installed Capacity (Net ICR)(b) | 32,588 | 33,114 | 33,529 | 33,855 | N/A | 34,600 | 35,000 | 35,400 | 35,800 | 36,100 |
| Assumed unavailable capacity | −2,100 | −2,100 | −2,100 | −2,100 | −2,100 | −2,100 | −2,100 | −2,100 | −2,100 | −2,100 |
| Total net capacity(c) | 30,488 | 31,014 | 31,429 | 31,755 | N/A | 32,500 | 32,900 | 33,300 | 33,700 | 34,000 |
| Operable capacity margin(d) | −2,357 | −2,311 | −2,441 | −2,625 | N/A | −2,665 | −2,635 | −2,580 | −2,540 | −2,570 |

(a)	The 2,375 MW value of operating reserves is based on the following assumptions: a first contingency of 1,400 MW plus a 25% increase in the 10-minute operating reserve to compensate for nonperformance of the reserve generating units (as discussed in Section 4.3.1) equal to 350 MW, and 30-minute reserves of 625 MW (one half of 1,250 MW).

(b) 	Net ICR values for 2014/2015 to 2017/2018 are the latest values approved by FERC. These net ICR values were developed using 2013 CELT Report loads. The ICR values for other years are consistent with the representative future net ICR values in Table 4-1.

(c) 	The net capacity values are equal to the net ICR minus the assumed unavailable capacity.

(d) 	“Operable capacity margin” equals “total net capacity” minus “total requirement.”

Figure 4-1 and Table 4-10 show that New England could have experienced larger negative operable capacity margins of approximately 2,360 MW as early as summer 2014 if the 90/10 peak loads occurred. Thus, throughout the study period, New England would need to rely on load and capacity relief from OP 4 actions under the projected 90/10 peak loads. Assuming the exact amount of resources needed to meet the 0.1 day per year loss-of-load expectation (LOLE) analysis is purchased in the FCA, this negative operable capacity margin would increase to approximately 2,625 MW by 2017. Using an indicative reserve margin of 14.2%, the operable capacity margin stays relatively constant from 2019 through 2023 in the negative 2,540 MW to negative 2,665 MW range.

## Identifying New England’s Generating Resources

Table 4-11 shows the megawatt amount of summer seasonal claimed capability of the generating resources, both systemwide and for each RSP subarea, categorized by the assumed operating classification of the resource.

Table 4-11 
2014 Summer Seasonal Claimed Capability for ISO New England Generating Resources,
by Assumed Operating Classification, Systemwide, and by RSP Subarea (MW)

| Area | Baseload(a) | Intermediate(b) | Peaking(c) | Intermittent(d) |
| --- | --- | --- | --- | --- |
| BHE | 125 | 488 | 159 | 58 |
| BOSTON | 676 | 1,655 | 305 | 9 |
| CMA/NEMA | 46 | 75 | 29 | 39 |
| CT | 3,898 | 718 | 551 | 5 |
| ME | 338 | 244 | 133 | 136 |
| NH | 2,828 | 1,183 | 83 | 86 |
| NOR | – | – | 170 | – |
| RI | 1,510 | 3,696 | 35 | 15 |
| SEMA | 1,866 | 1,369 | 142 | 38 |
| SME | 872 | 515 | 32 | 5 |
| SWCT | 542 | 971 | 768 | 3 |
| VT | 799 | – | 127 | 64 |
| WMA | 372 | 1,363 | 1,956 | 75 |
| Total(e) | 13,872 | 12,277 | 4,489 | 535 |

(a) 	Baseload units are assumed to run for long continuous hours at a constant output and have little flexibility. For operating classification purposes, bio/refuse, coal, fuel cell, pondage hydro, weekly hydro, nuclear, and thermal steam generators are assumed in the baseload category.

(b)	Intermediate units have the ability to dispatch flexibly and can follow variations in the system load. Combined-cycle (CC) generators are assumed in the intermediate category.

(c)	Peaking generators can be dispatched to meet peak demand for relatively short periods. Internal combustion, gas turbine, and pumped-storage generators are assumed in the peaking category.

(d)	Intermittent units produce energy subject to variations in “fuel” determined by weather. Run-of-river hydro, photovoltaic, and wind generators are assumed in the intermittent category.

(e)	Totals may not equal the sum because of rounding.

### Existing Generating Resources in New England

Generating units located close to load centers typically reduce the need for transmission system improvements. Table 4-12 tabulates the existing generating amounts and locations by RSP subarea, load zone, and state.

Table 4-12
RSP14 Generating Capacity by Subarea, Load Zone, and State, 2014

| RSP Subarea | State | Load Zone | Summer |  |  | Winter |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Capacity Rating (MW)(a) | % of RSP Subarea | % of State | Capacity Rating (MW)(a) | % of RSP Subarea | % of State |
| BHE | Maine | ME | 830 | 100 | 27 | 919 | 100 | 27 |
| ME | Maine | ME | 851 | 100 | 27 | 939 | 100 | 28 |
|  |  | NH | 0.4 | 0 | 0 | 0.4 | 0 | 0 |
|  |  |  | 852 | 100 | 27 | 939 | 100 | 28 |
| SME | Maine | ME | 1,424 | 100 | 46 | 1,535 | 100 | 45 |
| NH | New Hampshire | ME | 0 | 0 | 0 | 0 | 0 | 0 |
|  |  | NH | 4,147 | 99 | 100 | 4,285 | 99 | 100 |
|  |  |  | 4,148 | 99 | 100 | 4,286 | 99 | 100 |
|  | Vermont | NH | 1 | 0 | 0 | 1 | 0 | 0 |
|  |  | VT | 32 | 1 | 3 | 31 | 1 | 3 |
|  |  |  | 33 | 1 | 3 | 32 | 1 | 3 |
|  |  |  | 4,180 | 100 | 103 | 4,318 | 100 | 103 |
| VT | New Hampshire | NH | 2 | 0 | 0 | 2 | 0 | 0 |
|  |  | VT | 4 | 0 | 0 | 4 | 0 | 0 |
|  |  |  | 6 | 1 | 0 | 6 | 1 | 0 |
|  | Vermont | NH | 88 | 9 | 8 | 90 | 9 | 8 |
|  |  | VT | 896 | 91 | 82 | 947 | 91 | 83 |
|  |  |  | 984 | 99 | 90 | 1,037 | 99 | 91 |
|  |  |  | 990 | 100 | 90 | 1,043 | 100 | 91 |
| BOSTON | Massachusetts | NEMA/Boston | 2,643 | 100 | 21 | 3,660 | 100 | 26 |
|  |  | WCMA | 1 | 0 | 0 | 0 | 0 | 0 |
|  |  |  | 2,644 | 100 | 21 | 3,660 | 100 | 26 |
| CMA/ NEMA | Massachusetts | SEMA | 1 | 0 | 0 | 0 | 0 | 0 |
|  |  | WCMA | 189 | 100 | 1 | 181 | 100 | 1 |
|  |  |  | 189 | 100 | 2 | 181 | 100 | 1 |
| WMA | Massachusetts | WCMA | 3,687 | 98 | 29 | 3,962 | 98 | 28 |
|  | Vermont | WCMA | 78 | 2 | 7 | 76 | 2 | 7 |
|  |  |  | 3,765 | 100 | 36 | 4,039 | 100 | 34 |
| SEMA | Massachusetts | RI | <1 | 0 | 0 | 0 | 0 | 0 |
|  |  | SEMA | 3,171 | 93 | 25 | 3,357 | 92 | 23 |
|  |  |  | 3,171 | 93 | 25 | 3,357 | 92 | 23 |
|  | Rhode Island | RI | 244 | 7 | 13 | 279 | 8 | 13 |
|  |  |  | 3,416 | 100 | 38 | 3,636 | 100 | 37 |
| RI | Connecticut | RI | 757 | 14 | 9 | 857 | 15 | 9 |
|  | Massachusetts | SEMA | 2,903 | 55 | 23 | 3,179 | 54 | 22 |
|  | Rhode Island | RI | 1,595 | 30 | 87 | 1,821 | 31 | 87 |
|  |  |  | 5,256 | 100 | 119 | 5,857 | 100 | 118 |
| CT | Connecticut | CT | 5,173 | 100 | 62 | 5,315 | 100 | 57 |
| SWCT | Connecticut | CT | 2,284 | 100 | 27 | 2,532 | 100 | 27 |
| NOR | Connecticut | CT | 170 | 100 | 2 | 544 | 100 | 6 |
| Total(b) |  |  | 31,173 |  |  | 34,518 |  |  |

        - The values shown are representative seasonal claimed capability based on the 2014 CELT.

        - Totals may vary because of rounding.

### Generating Units in the ISO Generator Interconnection Queue

The interconnection requests in the ISO’s Generator Interconnection Queue reflect the region’s interest in building new generation capacity. Figure 4-2 shows the capacity of the 56 active generation-interconnection requests in the queue by RSP subarea as of April 1, 2014. As shown, over 60% of the active projects are proposed in the BOSTON, SWCT, and SEMA subareas. The areas with the most active proposed capacity additions are the BOSTON, SWCT, and SEMA subareas, followed by BHE, ME, and WMA. Together, these six subareas have approximately 6,220 MW under study or development of 6,915 MW of active projects for New England.

Figure 4-2: Capacity of generation-interconnection requests by RSP subarea, November 1997 to April 2014.

Notes: All capacities are based on the projects in the ISO Generator Interconnection Queue as of April 1, 2014, that would interconnect with the ISO system. Projects involving only transmission or that did not increase an existing generator’s capacity were excluded. Projects with more than one listing in the queue, representing different interconnection configurations, were counted only once.

Table 4-13 shows a summary of the projects in the ISO Generator Interconnection Queue as of April 1, 2014. Since the first publication of the queue in November 1997, 106 generating projects (14,995 MW) out of 372 total generator applications (totaling 73,782 MW) have become commercial. Since the queue’s inception, proposed projects totaling approximately 51,872 MW have been withdrawn, reflecting a megawatt attrition rate of 70%. The 56 active projects in the queue total 6,915 MW. Figure 4-3 shows the resources in the ISO Generator Interconnection Queue, by state and fuel type, as of April 1, 2014. Figure 4-4 shows the total megawatts of the same resources by RSP subarea, and Figure 4-5 shows the fuel types by subarea, expressed as a percentage of the total.

Table 4-13
Summary of Queue Projects as of April 1, 2014

| Category of Projects | Projects | Total Capacity (MW) |
| --- | --- | --- |
| Commercial | 106 | 14,995 |
| Active(a) | 56 | 6,915 |
| Withdrawn | 210 | 51,872 |
| Total | 372 | 73,782 |

(a) 	Source: NEPOOL Participants Committee COO Report (April 2014), http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/prtcpnts/mtrls/2014/apr42014/coo_report_apr_2014.pdf.

Figure 4-3: Resources in the ISO Generator Interconnection Queue, by state and fuel type, as of April 1, 2014 (MW and %).

Notes: The “Other Renewables” category includes wood, solar, and fuel cell capacity. The totals for all categories reflect all queue projects that would interconnect with the system and not all projects in New England.

Figure 4-4: Resources in the ISO Generator Interconnection Queue, by RSP subarea and fuel type, as of April 1, 2014 (MW).

Figure 4-5: Percentage of resources in the ISO Generator Interconnection Queue, by RSP subarea and fuel type, as of April 1, 2014.

In addition to the capacity issues discussed in Section 4, generating units must be readily available and able to meet the energy demands of load. The region has immediate and growing concerns about the availability of generating units to produce electrical energy, especially natural gas-fired and oil-fired generating units during winter peak periods. Fuel certainty is required to improve generator availability, as discussed in Section 6.2.

## Summary

Recent requests for resource retirements and the results of FCA #8 show that New England will have a resource shortfall through 2023 without the addition of new resources. Because additional resources are likely to retire, the ISO is working with stakeholders to identify issues and find the means of meeting future capacity needs. Recently, most new capacity resources have been demand resources (mainly energy efficiency) and imports from neighboring regions, and approximately 6,900 MW of proposed generation are in the ISO Generator Interconnection Queue. The ISO is committed to procuring adequate demand and supply resources and remains hopeful that the region will install adequate demand and supply resources in time to meet the physical capacity needs the ICRs will establish for future years.

By design, the level of the ICR specified for New England could necessitate the use of specific OP 4 actions because the ICR calculation includes capacity and accounts for the load relief these actions provide. Several factors would affect the frequency and extent of OP 4 actions, including the amount of resources procured to meet capacity needs, their availability, and actual system loads. Operable capacity study results show that the need for load and capacity relief by OP 4 actions will be approximately 2,600 MW during extremely hot and humid summer peak-load conditions. This amount is likely achievable through OP 4 actions by depleting operating reserves, scheduling emergency transactions with neighboring systems, operating real-time emergency generators, and implementing 5% voltage reductions.

This section shows that the region could meet representative operating-reserve requirements for the system as currently planned. Fast-start resources with a short lead time for project development can satisfy near-term operating-reserve requirements while providing operational flexibility to major load pockets and the system overall. Properly locating and sizing economical baseload generation within major load pockets decreases the amount of reserves required within the load pocket and reduces the reliance on transmission facilities. Transmission improvements also can allow for the increased use of reserves from outside these areas.

Preserving the reliable operation of the system will become increasingly challenging with potential retirements and the need for operating flexibility, particularly in light of the reliance on natural gas resources. These factors are expected to increase the need for reliable resources, especially those able to provide operating reserves and ramping capabilities. To begin addressing this need, the ISO has procured additional 10-minute reserves and replacement operating reserve.

Analysis and adjustments of the markets may be required to ensure that the region has reliable amounts of needed resources and operating reserves. One major near-term enhancement to the FCM involves the modification of the zonal structure used in the capacity market. The ISO has been working with stakeholders to implement criterion and processes for creating, modifying, or collapsing capacity zones, as appropriate. Other enhancements to the FCM and the FRM also may be considered to better meet operational needs. Additional approved and planned market incentives, including a sloped demand curve for use in the FCM, will further increase the likelihood of resource development where and when needed (refer to Section 6.2.4.1).

Section 6 discusses the region’s immediate concerns about the availability of natural-gas-fired and oil-fired generating units and their fuel certainty to produce electrical energy, especially during winter peak periods. That section also discusses the region’s Strategic Planning Initiative and other stakeholder efforts to address these challenges over the long term.

# Transmission Security and Upgrades

The ISO and regional stakeholders have made progress analyzing the transmission system in New England, developing “backstop” transmission solutions to address existing and projected transmission system needs and implementing these solutions. All 14 major 345 kV projects that have emerged from these efforts are critical for maintaining transmission system reliability. These transmission upgrades also have improved and will continue to improve the economic performance of the power system.

As of June 1, 2014, 11 of the 14 major projects have been placed in service, which include the following:

- Two Southwest Connecticut Reliability Projects (Phase 1 and Phase 2)

- Boston 345 kV Transmission Reliability Project (Phase 1 and Phase 2)

- Northwest Vermont (NWVT) Reliability Project

- Northeast Reliability Interconnection (NRI) Project

- New England East–West Solution (NEEWS)

  - Greater Springfield components

  - Rhode Island component

- SEMA

  - Short-Term Lower SEMA Upgrades

  - Long-Term Lower SEMA Upgrades

- Vermont Southern Loop Project

The Maine Power Reliability Program (MPRP) is currently under construction. The Interstate Reliability Project (Interstate) component of NEEWS has received siting approval and is currently under construction. One new 345 kV project has emerged as a result of the Greater Boston study. This solution is being reassessed as final project solutions are determined.

Figure 5-1 shows the approximate geographic region of each of these projects.

Figure 5-1: Approximate geographic region of each of the 14 major transmission projects in New England, as of June 1, 2014.

The 345 kV substations added across New England have improved the ability of the transmission system to meet load growth. These and other projects will help maintain system reliability and enhance the region’s ability to support a robust, competitive wholesale power market by reliably moving power from various internal and external sources to the region’s load centers.

This section discusses the need for transmission security and the performance of the transmission system in New England. It addresses the need for transmission upgrades—accounting for known plans for resource additions and attritions—and updates the progress of the current major transmission projects in the region. Previous RSPs, various PAC presentations, and other ISO reports contain information regarding the detailed analyses associated with many of these efforts. The draft Transmission Planning Process Guide contains details on the existing regional system planning process and how transmission planning studies are performed through the open regional stakeholder process (see Section 7.4.3). The draft Transmission Planning Technical Guide includes details on the current standards, criteria, and assumptions used in transmission planning studies. The ISO has received valuable stakeholder feedback on its current practices and is reviewing the bases for these practices.

## The Need for Transmission Security

A reliable, well-designed transmission system is essential for complying with mandatory reliability standards and providing regional transmission service that provides for the secure dispatch and operation of generation and that delivers numerous products and services, as follows:

- Capacity

- Electric energy

- Operating reserves

- Load-following

- Automatic generation control

- Immediate contingency response to sudden generator or transmission outages

A secure transmission system also plays an important role in the following functions:

- Improving the reliability of and access to supply resources

- Regulating voltage and minimizing voltage fluctuations

- Stabilizing the grid after transient events

- Facilitating the efficient use of regional supply and demand resources

- Reducing the amount of reserves necessary for the secure operation of the system

- Facilitating the scheduling of equipment maintenance

- Assisting neighboring balancing authority areas, especially during major contingencies affecting their reliability, and ensuring the reliability of the interconnected system

## Types of Transmission Upgrades

Attachment N of the OATT, “Procedures for Regional System Plan Upgrades,” defines several categories of transmission upgrades that can be developed to address various types of defined system needs, such as reliability and market efficiency.

### Reliability Transmission Upgrades

Reliability Transmission Upgrades are necessary to ensure the continued reliability of the New England transmission system in compliance with applicable reliability standards. A Reliability Transmission Upgrade also may provide market-efficiency benefits. To identify the transmission system facilities required to maintain reliability and system performance, the ISO evaluates the following factors using reasonable assumptions for forecasted load and the availability of generation and transmission facilities (based on maintenance schedules, forced outages, or other unavailability factors):

- Known changes in available supply resources and transmission facilities, such as anticipated transmission enhancements considering Elective Transmission Upgrades (ETUs) and merchant transmission facilities (MTFs) (see below); the addition of demand-side resources or new or previously unavailable generators; or generator retirements

- Forecasted load, which accounts for growth, reductions, and redistribution throughout the grid

- Acceptable stability response

- Acceptable short-circuit performance

- Acceptable voltage levels

- Adequate thermal capability

- Acceptable system operability and responses (e.g., automatic operations, voltage changes)

### Market Efficiency Transmission Upgrades

Market Efficiency Transmission Upgrades (METUs) primarily are designed to reduce the total net production cost to supply the system load. The ISO categorizes a proposed transmission upgrade as a METU when it determines that the net present value of the net reduction in the total cost to supply system load is greater than the net present value of the carrying cost of the identified upgrade. A Reliability Transmission Upgrade may qualify for interim treatment as a Market Efficiency Transmission Upgrade if market efficiency is used to advance the schedule for the implementation of the upgrade.

In determining the net present value of the costs of power system resources, the ISO takes into account applicable projected economic factors, as follows:

- Energy costs

- Capacity costs

- Cost of supplying total operating reserve

- System losses

- Changes in available supply resources and transmission facilities, such as through anticipated transmission enhancements considering Elective Transmission Upgrades and merchant transmission facilities (see below); the addition of demand-side resources or new or previously unavailable generators; or generator retirements

- Load growth

- Fuel costs and availability

- Generator availability

- Release of locked-in generating resources

- Present-worth factors for each project specific to the owner of the project

- Present-worth period not to exceed 10 years

- Cost of the project

Analyses can include historical information from market reports and special studies, for example, and they report on cumulative net present value annually over the study period.

### Generator Interconnection Upgrades and Generator Interconnection-Related Upgrades

A Generator Interconnection Upgrade is an addition or modification to the New England transmission system for interconnecting a new or existing generating unit whose energy or capacity capability is materially changing and increasing, whether or not the interconnection is for meeting the Network Capability Interconnection Standard or the Capacity Capability Interconnection Standard. Costs of Generator-Interconnection-Related Upgrades typically are allocated to the generator owner in accordance with the OATT. Generator-Interconnection-Related Upgrades to the New England transmission system are included in the RSP Project List for informational purposes (see Section 5.3).

### Elective Transmission Upgrades and Merchant Transmission Facilities

- An Elective Transmission Upgrade is an interconnection or upgrade to the pool transmission facilities that are part of the New England transmission system and subject to the ISO’s operational control pursuant to an operating agreement. ETUs are independently funded by one or more entities that have agreed to pay for all the costs of the upgrade. ETUs are not Reliability Transmission Upgrades, METUs, Generator-Interconnection-Related Upgrades, or projects proposed as an ETU but first identified as a transmission project in the RSP before its proposal as an ETU.

The Elective Transmission Upgrade process is the mechanism available to integrate merchant transmission facilities into the regional transmission system. MTFs are independently developed facilities over which its investors assume the full market risk of development. The ISO has initiated an effort to improve the existing ETU process.

## RSP Project List and Projected Transmission Project Costs

The RSP Project List is a summary of needed transmission projects for the region and includes information on project type, the primary owner, the transmission upgrades and their status, and the estimated cost of the pool transmission facility (PTF) portion of the project. The ISO updates this list at least three times per year. Additional information on the project classifications included in the RSP Project List is available in the draft Transmission Planning Process Guide.

The ISO regularly updates the PAC on study schedules, scopes of work, assumptions, draft and final results, and project costs and compiles the status of all projects in the RSP Project List. Projects are considered part of the Regional System Plan consistent with their status and are subject to transmission cost allocation for the region. RSP14 incorporates information from the June 2014 RSP Project List. As of June 2014, the total estimated cost of transmission upgrades—proposed, planned, and under construction—was approximately $4.5 billion, as shown in Table 5-1.

Table 5-1
Estimated Cost of Reliability Projects as of June 2014 Plan Update (Million $)

| Projects | Project Costs (millions of $)(a) |
| --- | --- |
| Major projects |  |
| Maine Power Reliability Program | 1,453 |
| Merrimack Valley/North Shore Reliability Project | 155 |
| Long-Term Lower SEMA Upgrades | 114 |
| New England East–West Solution (NEEWS) | 1,886 |
| NEEWS (Greater Springfield Reliability Project)—$718 million |  |
| NEEWS (Rhode Island Reliability Project)—$305 million |  |
| NEEWS (Interstate Reliability Project)—$510 million |  |
| NEEWS (other)—$74 million |  |
| Greater Rhode Island Transmission Reinforcements (including Advanced NEEWS) | 151 |
| Pittsfield/Greenfield Project | 146 |
| Greater Boston—North, South, Central, Western Suburbs | 695 |
| New Hampshire Solution—Southern, Central, Seacoast, Northern | 336 |
| Vermont Solution—Northwestern, Central, Southeastern | 93 |
| Southwest Connecticut | 295 |
| Subtotal(b) | 5,324 |
| Other projects(c) | 5,858 |
| New projects(d) | 18 |
| Projects whose cost estimates were previously reported as “to be determined”(d) | 0 |
| Total(b) | 11,200 |
| Minus “concept” projects | −119 |
| Minus “in-service” projects | −6,595 |
| Aggregate estimate of active projects in the plan(b) | 4,485 |

(a) 	Transmission owners provided all estimated costs, which may not meet the guidelines described in Planning Procedure No. 4, Procedure for Pool-Supported PTF Cost Review, Attachment D, “Project Cost Estimating Guidelines” (September 17, 2010), http://www.iso-ne.com/rules_proceds/isone_plan/pp04_0/pp4_0_attachment_d.pdf.

(b) 	Totals may not sum exactly because of rounding.

(c) 	"Other Projects" is the sum of all other project costs in the RSP Project List not explicitly listed above.

(d) 	Reflects updated costs from the June 2014 project list update compared with the March 2014 update.

The PTO Administrative Committee provides annual informational filings to FERC on the current regional transmission service rates and annual updates to the ISO and NEPOOL on projected regional transmission rates, as shown in Table 5-2.

Table 5-2
Actual and Forecast Regional Transmission Service Rates, 2013 to 2018(a)

|  | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 |
| --- | --- | --- | --- | --- | --- | --- |
|  | Actual(b) |  | Forecast(c) |  |  |  |
| Forecasted added transmission revenue requirements ($ millions)(d) | N/A | N/A | 880 | 834 | 843 | 738 |
| Revenue requirement increase from prior year ($ millions) | 204 | 155 | 143 | 134 | 144 | 116 |
| Total revenue requirement | 1,723 | 1,878 | 2,021 | 2,155 | 2,299 | 2,415 |
| Year prior 12 CP (kW)(e) | 20,189,256 | 20,910,580 | 20,910,580 | 20,910,580 | 20,910,580 | 20,910,580 |
| RNS rate increase from prior year ($/kW-year) | 10 | 4.5 | 7 | 6 | 7 | 5 |
| RNS rate ($/kW-year) | 85.32 | 89.80 | 97 | 103 | 110 | 115 |
| RNS rate forecast using a 53.9% load factor) ($/kWh)(d) | N/A | N/A | 0.020 | 0.022 | 0.023 | 0.024 |
| TOUT service rate ($/kW-hr) | 0.0097 | 0.0103 | 0.011 | 0.012 | 0.013 | 0.013 |

        - The figures may not agree because of rounding.

        - Sources: PTO Administrative Committee Annual Working Group: “Annual Informational Filing Regarding ISO Tariff Charges in Effect as of June 1, 2012, Pursuant to Docket Nos. RT04-2-000, et al.” (July 31, 2012), www.iso-ne.com/stlmnts/iso_rto_tariff/supp_docs/2012/pto_ac_info_filing_073012.pdf; “Supplement to July 31, 2013, Annual Informational Filing Regarding ISO-NE Tariff Charges in Effect as of June 1, 2013, Pursuant to Docket Nos. RT04-2-000, et. al.” (December 20, 2013), www.iso-ne.com/stlmnts/iso_rto_tariff/supp_docs/2013/pto_ac_info_filing_122013.pdf; and “Annual Informational Filing Regarding ISO Tariff Charges in Effect as of June 1, 2014, Pursuant to Docket Nos. RT04-2-000, et al.” (July 31, 2014), www.iso-ne.com/stlmts/iso_rto_tariff/supp_docs/2014/pto_ac_info_filing_073114.pdf.

(c) 	Source: RNS Rates: 2014–2018 PTF Forecast, PTO Administrative Committee Rates Working Group presentation at the NEPOOL Reliability Committee/Transmission Committee Summer Meeting (August 11–12, 2014), www.iso-ne.com/committees/comm_wkgrps/trans_comm/tariff_comm/mtrls/2014/aug11122014/a8_rns_5_yr_forecast.ppt. The 2015-2018 rate forecast reflects PTO Administrative Committee estimated data and assumptions and is preliminary and for illustrative purposes only. Therefore, such estimates, assumptions, and rates are expected to change as current data become available.

(d) 	Includes the forecasted annual pool-supported PTF revenue requirements for facilities expected to be placed in service and “construction work-in-progress” costs.

(e)	“12 CP” refers to the average of all the monthly regional network loads (per the OATT, Section 21.2) for the 12 months of the calendar year on which the rate is based.

## Transmission System Performance Needs Assessments and Upgrade Approvals

The New England power system provides electricity to a diverse region, ranging from rural agricultural areas to densely populated urban areas, and it integrates widely dispersed and varied types of power supply resources. The geographic distribution of peak loads in New England is approximately 20% in the northern states of Maine, New Hampshire, and Vermont and 80% in the southern states of Massachusetts, Connecticut, and Rhode Island. Although the land area in the northern states is larger than the land area in the southern states, the greater urban development in southern New England creates the relatively larger demand and corresponding transmission density.

The New England transmission system consists of mostly 115 kV, 230 kV, and 345 kV transmission lines, which in northern New England generally are longer and fewer in number than in southern New England. The New England area has nine interconnections with New York: two 345 kV ties; one 230 kV tie; one 138 kV tie; three 115 kV ties; one 69 kV tie; and one 330 MW, ±150 kV high-voltage direct-current (HVDC) tie.

New England and New Brunswick are connected through two 345 kV ties, the second of which was placed in service in December 2007. New England also has two HVDC interconnections with Québec: a 225 MW back-to-back converter at Highgate in northern Vermont and a ±450 kV HVDC line with terminal configurations allowing up to 2,000 MW to be delivered at Sandy Pond in Massachusetts.

Because of the age of the transmission system in New England, many assets are reaching their end of life and are requiring significant refurbishment. These activities are spread across the system and are being addressed either individually or as part of an ongoing solutions assessment. Upgrades associated with asset condition have been ongoing for years, and from June 2013 to June 2014, equipment owners have made the following presentations to stakeholders:

- Section 242 Rebuild (Winslow to Heywood Road)

- Transmission Facility Refurbishments, Update to Salem Harbor Cable-Replacement Solution

- Asset-Condition Needs: 115 kV Salem Harbor Substation

- Old Town Substation Solutions Study

- Sandy Pond AC Substation Refurbishment

- Housatonic River Crossing (HRX)

- New England Transmission Line Asset-Condition Refurbishment Program and Projects

- PV20 Cable Replacement

- Baird Substation Solutions Study

The following sections summarize the June 2014 status of several transmission planning studies and projects and the need for upgrades.

### Northern New England

The northern New England (NNE) area encompasses the transmission system in Maine, New Hampshire, and Vermont. Studies of each of these states are being conducted to address the transmission system’s short-term and long-term needs.

#### Northern New England Transmission

New England and New Brunswick have two 345 kV interconnections leading into a 345 kV corridor at Orrington, Maine. The corridor spans hundreds of miles and eventually ties into Massachusetts. The transmission system throughout northern New England is limited in capacity; it is weak in places and faces numerous transmission security concerns. Underlying the limited number of 345 kV transmission facilities are a number of old, low-capacity, and long 115 kV lines. These lines serve a geographically dispersed load, as well as the concentrated, more developed load centers in southern Maine, southern New Hampshire, and northwestern Vermont.

The two most significant issues facing the area have been to maintain the general performance of the long 345 kV corridor, particularly through Maine, and to ensure sufficient system security to meet demand. The region faces thermal and voltage performance issues and stability concerns and is reliant on several special protection systems (SPSs) that may be subject to incorrect or undesired operation. The system of long 115 kV lines, with weak sources and high real- and reactive-power losses, is exceeding its ability to integrate generation and efficiently and effectively serve load. Also, in many instances, the underlying systems of 34.5 kV, 46 kV, and 69 kV lines are exceeding their capabilities and are being upgraded, placing greater demands on an already stressed 115 kV system.

Over the past several years, the addition of generation in Maine and New Hampshire, in combination with the area’s limited transfer capability and limited transmission expansion, has increased the likelihood of many northern New England interfaces operating near their limits, creating restrictions on northern resources. Because these interface limits depend on generation dispatch, the operation of the system becomes more complex. Additional concerns in northern New England include limited system flexibility to accommodate maintenance outages, limited dynamic reactive-power resources, and high real- and reactive-power losses. Power flows on some interfaces, which historically have been from north to south, at times have reversed and are moving from south to north, highlighting shifting market economics, generation dispatch patterns, and emerging system weaknesses, in addition to those already identified on the interfaces. The recent operating data in this corridor shows that flows remain predominantly in the north to south direction.

A significant number of new wind generation projects have interconnected to the northern portions of the New England transmission system. Several additional proposed wind projects have applied to interconnect in these areas (see Section 4.5.2). These portions of the system are remote from the region’s load centers and are susceptible to poor voltage performance. To date, new wind generation constructed in New England provides limited dynamic voltage support. These locations have also experienced generation restrictions in system operations, especially during transmission-system-maintenance conditions. These type of restrictions are expected to continue in the absence of significant transmission expansion. Refer to Section 6.6 for a discussion of wind-integration activities.

#### Northern New England Transmission System Studies

Study efforts are progressing in various portions of Maine, New Hampshire, and Vermont to address a number of transmission system concerns. Some of these studies have focused on defining short-term needs and developing solutions, while others have made significant progress in evaluating potential system conditions 10 years into the future.

Maine—The long-term system needs of Bangor Hydro Electric (BHE) and Central Maine Power (CMP) were identified in 2007. To improve the performance of the Bangor system, the Keene Road substation was completed and 115 kV upgrades have been placed into service. CMP has placed in service 115 kV expansions in western Maine to address area thermal and voltage issues. Upgrades north of Augusta and near Rumford have reduced some voltage concerns. Several 115 kV system reinforcements, including the addition of the new substations at Maguire Road and Larrabee Road in southern Maine, already have been placed into service and are helping serve southern Maine load in the near term.

Projects planned as part of the Maine Power Reliability Program must meet reliability requirements and be consistent with long-term planning objectives in both the BHE and CMP service territories. These projects include the addition of significant new 345 kV and 115 kV transmission facilities and new 345 kV autotransformers at key locations.

The northern portion of the Maine transmission system continues to present challenges for reliable system planning and operations. Lengthy sections of 345 kV transmission in Maine connect the New Brunswick system to the greater New England network. Until the addition of the MPRP project (see Section 5.4.1.3), portions of this corridor consisted of only one 345 kV line in parallel with relatively weak 115 kV transmission serving small amounts of load. To maintain reliable operations, this part of the system currently employs several SPSs, and a static VAR compensator (SVC) provides dynamic voltage support. Certain contingencies have the potential to cause high voltages, low voltages, high frequencies, the loss of a large amount of generation, or system separation from New Brunswick. A number of new generation projects and Elective Transmission Upgrades are seeking to interconnect to this part of the system. The technical complexities mentioned complicate the system’s ability to accommodate additional interconnections.

A transfer study identified the increase in transfer capability across the major interfaces in Maine and neighboring systems resulting from the addition of the MPRP project. The study, completed in 2012, evaluated thermal, voltage, and stability transfer limits and demonstrated a modest increase in transfer capability across the major interfaces in Maine, including Maine to New Hampshire. The overall limiting condition in setting the new transfer limits is the system’s stability response to faults in southern New England. The new transfer limits have been adopted in the appropriate planning and capacity market processes. The resulting new transfer limits indicate that the constraints within Maine will likely continue to limit the ability of the system to deliver some existing and new capacity.

In addition to the Surowiec South and Orrington South interfaces, subarea export constraints will continue to be restrictive after the updated MPRP transfer limits are put in place. They include the Rumford Area, Bigelow/Upper Kennebec, and Northern Maine/Keene Road. Additional local constraints may emerge as more resources pursue interconnection.

In late 2013, a new needs assessment was initiated for the Maine portion of the transmission system. The study will identify needs for 2023.

New Hampshire—A number of studies of the New Hampshire portion of the system have been conducted. These studies have identified the need for additional 345/115 kV transformation capability and the need for additional 115 kV transmission support in various parts of the state. Existing and midterm concerns of northern and central New Hampshire have been improved by closing the Y-138 tie (between Saco Valley and White Lake) with Maine and the addition of a second 345/115 kV autotransformer at Deerfield.

As discussed below, a 10-year, two-phase study of the New Hampshire area has been completed as part of the Vermont/New Hampshire Transmission System Needs Assessment and Solutions Study.

Vermont—Vermont regulations require the Vermont Electric Power Company (VELCO), the owner and operator of Vermont's transmission system, to develop a 20-year Vermont Long-Range Transmission Plan every three years. The 2012 Vermont Long-Range Plan identifies four regional groupings of reliability needs on Vermont’s high-voltage electric power system (115 kV and above), which are consistent with the regional system plan findings described below.

The Vermont system was studied to assess and resolve potential reliability issues as part of the Vermont/New Hampshire Transmission System 2011 Needs Assessment. Collaborative efforts among the ISO, VELCO, National Grid, and Northeast Utilities have continued assessing the reliability of Vermont and New Hampshire’s transmission system.

New Hampshire and Vermont Combined—A combined study of the Vermont and New Hampshire area was completed in two phases. The first phase was to conduct the Vermont/New Hampshire Transmission System 2011 Needs Assessment, which identified and focused on transmission system needs for serving New Hampshire and Vermont loads while maintaining overall regional system performance. The second phase studied transmission solution alternatives and resulted in proposed regulated transmission solutions that address the violations identified in the needs assessment. In addition, a pilot study analyzing market resource alternatives in load pockets was conducted for the Vermont/New Hampshire system.

The Vermont/New Hampshire Transmission System 2011 Needs Assessment identified several areas of weak performance and demonstrated the following transmission system needs:

- The Vermont transmission system: The Vermont transmission system requires additional local reactive support to help maintain voltage within criteria. In addition, following the outage of critical facilities that serve the area, the remaining 115 kV lines serving the state become loaded above emergency limits. This indicates the need for locating additional resources within that area or adding transmission capacity to maintain reliable operations following these contingencies.

- Multiple outages: The combination of key line contingencies causes some thermal overloads and many low-voltage violations on the underlying 115 kV system.

- Concord–Manchester–Nashua: This area, stretching roughly from the Webster substation in the north to the Power Street substation in the south, shows many voltage and thermal violations for a wide range of first and second contingencies. These violations are more significant when certain generation connected to the system is unavailable.

- Central New Hampshire: The portion of New Hampshire’s transmission system near the Beebe River substation shows many post-contingency voltage violations, which in turn cause some thermal overloads on 115 kV lines.

- The New Hampshire seacoast: The New Hampshire seacoast area is in need of additional resources or transmission capability to serve the 115 kV network under both N-1 and N-1-1 conditions.

- Western New Hampshire: The New Hampshire western area shows many post-contingency voltage violations and thermal overloads on 115 kV lines under both N-1 and N-1-1 conditions.

- Other areas of the New Hampshire system: Other regions of the system show violations, illustrating a dependence on local generation and sensitivity to area load growth. As solutions are developed to meet the needs identified for the larger areas, the needs of these areas may be addressed; however, the smaller areas should continue to be monitored throughout the planning process to ensure their compliance with planning criteria.

The Vermont/New Hampshire Transmission System 2011 Needs Assessment identified the critical load level at which the voltage violations and thermal overloads would occur. Most of the voltage and thermal violations identified were found at or below existing peak load levels under various system conditions. The needs assessment, coupled with the critical load level analysis, indicates the need to examine substantial transmission system upgrades to improve system performance.

The study reflected several sensitivities to future assumptions within New Hampshire and Vermont, such as changes to the status of Vermont Yankee (VY), which may have an impact on the performance of both the New Hampshire and Vermont transmission systems. In addition, the New York ISO (NYISO) has informed ISO New England that it cannot ensure that flow across the 115 kV PV-20 line between Plattsburgh substation in New York and Sand Bar substation in Vermont will be available when necessary to resolve New England’s system concerns. Contingencies currently exist on the New York Power Authority (NYPA) 230 kV system that limit New York’s ability to move power across this facility to New England. Even after system upgrades eliminate these contingencies, NYISO has recommended against relying on flow into Vermont across the PV-20 line. Furthermore, no additional contracts are in place across the facility to ensure that power would flow to New England as needed.

The New Hampshire/Vermont Solutions Study assessed alternatives for upgrading the New Hampshire and Vermont 345 kV and 115 kV transmission system. Transmission upgrades for ensuring the reliability of the transmission system in New Hampshire and Vermont were identified to address the reliability needs found in the needs assessment.

A follow-up analysis to the New Hampshire/Vermont Needs Assessments and Solutions Study included a reassessment of the preferred solutions developed in the solutions study. This reassessment incorporated an updated set of assumptions based on the 2011 “proof-of concept” long-term energy-efficiency forecast, as well as for load, generation and demand resources, transmission system topology, and the use of existing transmission system devices. The original NH/VT Solutions Study identified a number of transmission system upgrades, which no longer are required within the 10-year planning horizon and could be deferred from the preferred solution identified in the New Hampshire/Vermont Solutions Study. These deferred transmission system upgrades are located in several portions of the New Hampshire and Vermont transmission systems.

Another study of the New Hampshire/Vermont area was initiated in 2012 to capture the final long-term energy-efficiency forecast, as well as the latest Forward Capacity Auction results and the latest load forecast for 2022. This study was further updated to incorporate the announced retirement of the Vermont Yankee generator and to incorporate the 2013 CELT load forecast. This 2023 New Hampshire/Vermont Needs Assessment resulted in a number of adjustments to the previously identified preferred solutions for the area because of several deferred needs, as follows:

- In northwestern Vermont, a proposed special protection system to cross-trip the PV-20 line to mitigate low voltages following certain contingencies in New York has been cancelled.

- In southeastern Vermont, a section of the 381 (Vernon/Vermont border) 345 kV line upgrade has been cancelled.

- In central Vermont/Connecticut River, the new Coolidge–West Rutland 345 kV line has been cancelled

Additionally, the proposed new Coolidge–Ascutney 115 kV line is being reevaluated along with the alternative of rebuilding the existing line. In New Hampshire, the need to address voltage issues at the Amherst 345 kV substation was reconfirmed. The previously proposed upgrade of the 345 kV 326 line from Scobie, NH, to Sandy Pond, MA, is being reevaluated in coordination with the Greater Boston Needs Assessment and Solutions Study reassessments (see below).

The remaining transmission system upgrades, identified for each of the subareas in northern New England, are as follows:

Southwestern Vermont—The following solutions were developed to eliminate low voltages at Bennington:

- Adams 115 kV substation reconfiguration and the addition of two circuit breakers

- Two 12.5 megavolt-ampere reactive (MVAR) capacitor banks at the Bennington 115 kV substation

Southeastern Vermont and Western New Hampshire—The southeastern Vermont and western New Hampshire area focuses on the Vernon area in southern Vermont and the Fitzwilliam/Monadnock area in western New Hampshire. The Fitzwilliam/Monadnock area is centered on the Monadnock 115 kV bus. This area is bounded by the L163 Jackman–Keene line, the I135N Bellows Falls–Monadnock tap, the J136N Bellows Falls–Flagg Pond line, and the N186 Vernon Road tap–Chestnut Hill 115 kV lines, as well as the Fitzwilliam 345/115 kV autotransformer. The following solutions were developed to mitigate thermal overloads and voltage violations:

- New Fitzwilliam–Monadnock 115 kV line

- Two 13.3 MVAR capacitor banks at Weare 115 kV substation

- A152 Chestnut Hill–Westport–Swanzey 115 kV line rebuild

- N186-2 Vernon Road tap–Chestnut Hill 115 kV line rebuild

- Terminal upgrades at Flagg Pond 115 kV substation

Northern New Hampshire and Northern Vermont—The northern Vermont area refers to the area associated with the 115 kV path along northern Vermont between the St. Johnsbury and Highgate 115 kV stations. The northern New Hampshire area represents the northern 115 kV loop including Whitefield, Lost Nation, and Berlin, and the Comerford/Moore/Littleton area. The following solutions were developed to mitigate thermal overloads and voltage violations:

- Second 230/115 kV autotransformer at Littleton

- A 230 kV C203 Comerford–Moore line tap into Littleton substation

Central New Hampshire—The central New Hampshire area stretches roughly from the Webster substation in the south to the Littleton substation in the north. The following solutions were developed to mitigate thermal overloads and voltage violations:

- Four 26 MVAR capacitor banks at Webster 115 kV substation

- Two 25 MVAR dynamic reactive devices at Saco Valley 115 kV substation

- Load transfer scheme

Southern New Hampshire—The southern New Hampshire area stretches roughly from the Webster substation in the north to the Power Street substation in the south. This area is fed from local generation and from the Deerfield and Scobie 345/115 kV stations from the east, from the Webster 115 kV station from the north, the L163 Keene–Jackman 115 kV line from the west, and the Y151 Power St–Tewksbury 115 kV line from the south. This area serves the Nashua, Manchester, and Concord area loads and contains a significant portion of the total New Hampshire load. The following solutions were developed to mitigate multiple thermal overloads and voltage violations:

- 345/115 kV autotransformer at Eagle 115 kV substation

- Four 25 MVAR capacitor banks at Eagle

- 326-NU Scobie Pond–NH/MA border 345 kV line upgrade

- Scobie series circuit breaker with breaker 802

- New Scobie–Huse Road 115 kV line

- G146 Garvins–Deerfield 115 kV line upgrade

- P145 Oak Hill–Merrimack 115 kV line upgrade

- D118 Deerfield–Pine Hill 115 kV line rebuild

- H137 Merrimack–Garvins 115 kV line rebuild

- J114-2 Greggs–Rimmon 115 kV line upgrade

- Loop V182 line into Oak Hill substation (Garvins–Webster)

- Merrimack series circuit breaker with breakers BT12 and BT23

- Merrimack capacitor bank relocation within the substation

- K165 Eagle–Bridge St.–Power St. 115 kV line upgrade

New Hampshire Seacoast—The New Hampshire Seacoast area is the area along the New Hampshire coastline, bordered by the Deerfield and Scobie 115 kV stations to the west and the Three Rivers 115 kV station to the north. The area has no 115 kV connections to the south. This system serves load in the Portsmouth, Dover, and Rochester areas. The following solutions were developed to mitigate multiple thermal overloads and voltage violations:

- New Madbury–Portsmouth 115 kV line

- New Scobie–Chester 115 kV line

- Chester substation work associated with new 115 kV line

- Six 13.3 MVAR capacitor banks at Schiller 115 kV substation and series circuit breaker with breaker BT10

- H141 Chester–Great Bay 115 kV line upgrade

- R193 Scobie–Kingston tap 115 kV line upgrade

- Three Rivers 115 kV series circuit breaker with breaker R1690

#### Northern New England Transmission Projects

The ISO has identified projects that address issues with transmission system performance, either individually or in combination. Some of the projects, as described in the previous sections, address subregional reliability issues and have the ancillary benefit of improving the performance of major transmission corridors and thus the overall performance of the system. The projects are as follows:

- Deerfield Substation Expansion Project—This project adds a second 345/115 kV autotransformer at the Deerfield substation in New Hampshire, which entered service in November 2011. Three new 345 kV circuit breakers were also added to eliminate problematic contingencies. Five 115 kV circuit breakers were replaced, and one new 115 kV circuit breaker was added. To mitigate area overloads, the Madbury–Deerfield (L175) 115 kV line was rebuilt, and the Dover–Madbury (M183) 115 kV line and Deerfield–Rochester (C129) 115 kV line were reconductored. In addition, the Rochester substation was expanded to accommodate a new radial line to a new North Rochester substation in December 2013.

- Chester SVC Control System Replacement—This project is an in-kind replacement of the existing control system at Chester SVC. The project is needed because of equipment age and performance issues. The expected in-service date for the project is July 2014.

- Maine Power Reliability Program—The MPRP provides a 10-year look at the Maine transmission system and has identified the following inadequacies:

- Insufficient 345 kV transmission—Maine currently has two 345 kV transmission paths from southern to central Maine and two 345 kV ties from northern Maine to New Brunswick. In the central part of the system, Maine has a single 345 kV path.

- Insufficient 345/115 kV transformation capacity—The reliability of Maine’s 115 kV system depends on the capacity and availability of autotransformers at five locations. Overloads of the autotransformers under normal and contingency conditions illustrate insufficient transformation capacity.

- Insufficient 345 kV transmission support for Portland and southern Maine—The largest load pocket in Maine is subject to thermal and voltage reliability issues.

- Insufficient transmission infrastructure in western, central, and southern Maine regions—Each of these regions in Maine represents a major load pocket that depends on local generation to meet reliability standards.

- Insufficient transmission infrastructure in midcoast and “downeast” Maine regions—These regions in Maine (i.e., Bucksport−Eastport) represent load pockets that have no local generation and that fully depend on the transmission system.

- MPRP Transmission Alternatives Study—This study identified transmission upgrades to serve load pockets and ensure that the system will meet national and regional transmission reliability criteria. These projects will provide the ancillary benefit of facilitating the maintenance of the system in Maine. The selected alternative, referred to in the transmission alternatives study as “N5S1,” consists of significant additions of new 345 kV lines, 115 kV lines, 115 kV capacitors, and 345/115 kV autotransformers; line rebuilds; and the separation of circuits sharing common towers. The new 345 kV lines in the north will create a 345 kV path from Orrington to Surowiec, while the new 345 kV lines in the south will create a third parallel path from Surowiec to Eliot in southern Maine. While these new paths are expected to increase transfer capability out of Maine, they also will increase the ability to move power into Maine from New Hampshire and improve the ability of the transmission system within Maine to move power into the load pockets as necessary.

- The expected in-service date for most of the MPRP project is early 2015, with the rest scheduled for completion in early 2017. The major 345 kV components of the current plan are as follows:

- New 345 kV line construction

    - Orrington–Albion Road

    - Albion Road–Coopers Mills

    - Coopers Mills–Larrabee Road

    - Larrabee Road–Surowiec

    - Surowiec–Raven Farm

    - South Gorham–Maguire Road

    - Maguire Road–Eliot (formally called Three Rivers)

- New 345/115 kV autotransformers

    - Albion Road

    - Cooper Mills (replace existing Maxcys T3)

    - Larrabee Road

    - Maguire Road

    - South Gorham

- Separation of double-circuit towers (DCTs)

    - 345 kV Kennebec River Crossing by the Maine Yankee−Buxton and Maine Yankee−Surowiec circuits (375/377)

  - Rerating of 345 kV transmission lines

    - Section 378 (345 kV Maine Yankee–Mason)

### Southern New England

The southern New England area encompasses the Massachusetts, Rhode Island, and Connecticut transmission system. Studies of these states are being conducted to address a wide range of transmission system concerns, both short and long term.

#### Southern New England Transmission

The 345 kV facilities that traverse southern New England comprise the primary infrastructure integrating southern New England, northern New England, and the Maritimes Balancing Authority Area with the rest of the Eastern Interconnection. This network serves the majority of New England demand, integrating a substantial portion of the region’s supply, demand, and import resources.

Although recent improvements have been made, the southern New England system continues to face thermal, low-voltage, high-voltage, and short-circuit concerns under some system conditions. The most significant concerns involve maintaining the reliability of supply to serve load and developing the transmission infrastructure to integrate generation throughout this area. In many areas, an aging low-capacity 115 kV system has been overtaxed and is no longer able to serve load and support generation reliably. Upgrades to the power system are being planned and developed to ensure the system can meet its current level of demand and prepare for future load growth (see Section 3.1).

#### Southern New England Transmission System Studies

Study efforts in southern New England have been progressing on a wide range of system concerns. Initial efforts focused on load areas with the most significant risks to reliability and threats to the system, particularly Boston and Southwest Connecticut. With the completion of the 345 kV Reliability Project in Boston and the Phase I and Phase II Projects in Southwest Connecticut, plans are under development to address the reliability of other parts of the system, particularly eastern Connecticut; Rhode Island; and southeastern Massachusetts, including Cape Cod. Boston and Southwest Connecticut have been reevaluated to address the changes in load and resources that have occurred since the initial set of upgrades was established and solution plans have been developed. Additionally, solution plans have been developed for Greater Hartford, central Connecticut, and western and central Massachusetts.

Several needs, originally identified for a number of the upgrades associated with the New England East–West Solution studies have been reconfirmed. These include three of the four NEEWS components: the Rhode Island Reliability Project (RIRP), the Greater Springfield Reliability Project (GSRP), and the Interstate Reliability Project. The Interstate reassessment effort also addressed the much broader requirements of the overall New England east–west and west–east transmission systems.

The fourth NEEWS component, the Central Connecticut Reliability Project (CCRP), is being replaced by the upgrades that will address the needs established for the Greater Hartford/Central Connecticut (GHCC) study. The GHCC study includes the Hartford, Middletown, northwestern Connecticut, and Barbour Hill areas. In combination, this study, the Eastern Connecticut study, and the Southwest Connecticut study cover the entire load within the state. With the exception of the Eastern Connecticut study, solution alternatives have been developed for all the Connecticut studies.

The Boston area is being reevaluated to reflect recently made changes in the cable-rating assumptions for downtown Boston and the addition of Footprint Power’s 674 MW generation at the Salem Harbor site. The study also is continuing to evaluate two transmission proposals: (1) the previously preferred solution, proposed by National Grid and Northeast Utilities, which involves the expansion of the 345 kV AC system between New Hampshire and Massachusetts, and (2) an alternative solution proposed by New Hampshire Transmission, LLC that incorporates an HVDC submarine cable (SeaLink HVDC Submarine Cable Project) extending from Seabrook, New Hampshire, to Boston. Both alternatives incorporate several common AC system reinforcements.

Preferred solutions were developed for the Pittsfield–Greenfield area of western Massachusetts. The needs were reassessed using a 10-year horizon with the latest topology and load assumptions, as well as the energy-efficiency forecast. The results of the needs reassessment have shown that some parts of the preferred solution are no longer needed and some additional solution components need to be added.

A needs reassessment is in progress for the Southeast Massachusetts/Rhode Island (SEMA/RI) area, referred to as Eastern REMVEC, due to the retirement request for the Brayton Point station. On January 27, 2014, the owner of Brayton Point station provided notice that the station will be retired on or before June 1, 2017. Originally, major goals of the study were to determine any long-term system needs required to integrally serve the broad SEMA, NEMA, and Rhode Island areas and to ensure consistency and cohesiveness of the planning and design of these areas of the system. Under the needs reassessment, the major goals remain the same, with the addition of evaluating the area without the presence of the Brayton Point station.

Southern New England Region—The Rhode Island Reliability Project and the Greater Springfield Reliability Project were placed in service in 2013. The need for the Interstate and the CCRP components required a significant amount of revised analysis due to the following:

- New resources cleared in the Forward Capacity Market (see Section 4.1.3) within Connecticut and to the west of the New England East–West interface.

- The energy-efficiency forecast and the updated load forecast lowered the load forecast (see Section 3.2).

Because the need for the Interstate component of NEEWS was based on the transfer of power into eastern New England, western New England, Connecticut, and Rhode Island, the lower forecasted loads in these areas (as shown by the new load forecast combined with the energy-efficiency forecast) required a reassessment of the solution. The first needs assessment was published in April 2011, and the first solutions study was published in February 2012. The second versions of these documents both were published in September 2012.

The results of the September 2012 needs assessment and solutions study show system needs similar to those found in the April 2011 needs assessment, as well as the need for all parts of the preferred solution discussed below. The needs assessment shows a substantial need for an integrated regional transmission solution to resolve system performance issues in eastern New England, western New England, and Greater Rhode Island (GRI). The solutions studies show that the original interstate project is effective at resolving the majority of the overload issues in Rhode Island, western New England, Connecticut, and eastern New England. See Figure 5-2.

Figure 5-2: Map of constraints in southern New England.

The modifications to the original Interstate project reflect a reduced need to move power from eastern New England to serve load in western New England and Connecticut and the need to improve the transfer capability into Rhode Island. It also shows the increased need to move power from western New England to serve load in eastern New England below 2012 load levels. The new results also show the need to increase transfer capability into Connecticut and east to west at 2016 to 2017 load levels. Additionally, the revised analysis showed that the changes in resources and forecasted loads had reduced the need for increasing the transfer capability across the western Connecticut interface, which the 345 kV line of CCRP, the fourth major component of NEEWS, would have achieved. Since that 345 kV line would have been entirely within the area under study in the Greater Hartford/Central Connecticut study, the revaluation of CCRP was extended and combined with the GHCC study, with the expectation that both sets of needs could be addressed by a single set of integrated 115 kV solutions. The GHCC study is discussed in the “Connecticut” portion of this section. Concerns over the need to move power from western New England to eastern New England have been emphasized with the upcoming retirement of Brayton Point station on or before June 1, 2017.

Addressing the transmission constraints along the Card Street–West Medway corridor (CT–RI–MA) will resolve these load-serving issues. This also would reduce potential constraints surrounding the approximately 2,000 MW of generation along this corridor in the Greater Rhode Island area for reliably serving load in both western and eastern New England over the long-term planning horizon.

The original analysis showed the need for a third 345 kV line into West Farnum to reliably serve load in Rhode Island, and the updated needs assessment shows this need as well. The subsequent solutions studies reviewed five different alternatives to resolve the remaining needs, and the preferred alternative was a slightly modified version of the original Interstate project. As a result of the 2011 and 2012 evaluations, the necessary additional modifications to resolve all criteria violations for serving eastern New England load are as follows:

- Upgrade the 345 kV line from ANP Blackstone, MA, to NEA Bellingham, MA, to West Medway, MA (336 line)

- Reconductor the 345 kV line from Sherman Road, RI, to West Farnum, RI (328 line)

- Eliminate the sag limit on the 115 kV line from Montville, CT, to Buddington, CT (1410 line)

- Upgrade the terminal equipment at Sherman Road (345 kV), West Medway (345 kV), and West Farnum (345 kV) substations

- Rebuild the Sherman Road (345 kV) switching station

Because of the reassessment, the following upgrades included in the original Interstate Reliability Project are no longer needed:

- Upgrading the terminal equipment necessary to increase the ratings on the 345 kV line from ANP Blackstone, MA, to Sherman Road, RI (3361 line)

- Reconductoring a section of the 345 kV line from Sherman Road, RI, to Killingly, CT (347 line)

- Adding 480 MVARs of capacitors at the Montville 345 kV substation

- Adding a 345 kV circuit breaker at the Killingly substation

Another project originally part of the Interstate component of NEEWS, the looping of the Millstone–Manchester 345 kV line into the Card Street substation, is not needed as part of the IRP.

Massachusetts—

- Greater Boston area: A long-term reliability needs assessment has been completed for the Greater Boston area, and solutions have been developed to address the criteria violations that resulted. Because of significant changes in the study area, two updates have been released since the needs assessment report was published in 2010—the 2018 needs assessment and the 2023 needs assessment. The changes that prompted the updates can be categorized into four topics: load forecast and demand resources, resource additions and retirements, transmission system topology, and system modeling:

- Changes in load forecast and demand resources

The net load in the study area decreased by 200 MW in the 2023 needs assessment compared with the 2018 needs assessment

- Resource additions and retirements

The most significant change in the study area was the availability of generation resources. As a result of a nonprice retirement request (NPRR), the Salem Harbor station will be retired in 2014. This retirement reduces generation resources in the area by approximately 750 MW, representing a loss of over 20% of the area resources. Because of this retirement, upgrades to five transmission lines in the North Shore area, northwest of Boston, were identified and have been placed in service. These transmission upgrades were needed to address immediate reliability concerns in the area due to the retirement.

- Also because of the Salem Harbor retirement, a new resource was proposed, and it ultimately cleared the FCM in 2013 with an obligation to be in service by June 2016. The new generating facility has a capacity supply obligation of 674 MW.

- Transmission system topology

A number of solution alternatives were identified and advanced to resolve urgent needs in the Boston area. The following list summarizes these advanced upgrades:

  - 115 kV line reconductorings:

- 320-507/508 Lexington–Waltham 115 kV (in service)

- 128-518/P-168 Chelsea–Revere 115 kV (in service)

- C-129N/201-502 Depot St. tap–Medway 115 kV (in service)

- D-130/201-501 Depot St. tap–Medway 115 kV (in service)

- 211-508 Woburn–Burlington 115 kV (anticipated in-service date is November 2014)

  - New 115 kV line addition with switching station:

- 447-502 West Walpole–Holbrook 115 kV

- Three-breaker switching station at Sharon sectionalizing the 447-502, 447-508, and 447-509 lines, West Walpole–Holbrook

  - New autotransformer addition:

- 230/115 kV autotransformer at Sudbury

- 115 kV capacitor additions:

- A 115 kV 36.7 MVAR capacitor bank at Hartwell (in service)

- A 115 kV 36.7 MVAR capacitor bank at Chelsea (in service)

- 115 kV station reconfigurations:

- Swap the terminal locations of the 329-530 North Cambridge–Brighton 115 kV line and transformer #1 at North Cambridge

- Swap the terminal locations of the 329-531 North Cambridge–Brighton 115 kV line and transformer #4 at North Cambridge

- System modeling

In 2012, a significant study adjustment was made to take into account the updated ratings for the underground cable systems in the Boston area.

- The needs assessment results indicated a need to increase Boston import capability, as well as bolster the transmission system within the area, to serve the load reliably. Most of the needs observed in the 2018 needs assessment also were observed in the 2023 needs assessment, and most of the reliability issues exist at the 2013 load levels.

- Additionally, as part of the 2023 needs assessment, a minimum load level study was conducted to assess the system under minimum load conditions. The results of this testing indicated the need for shunt reactive compensation in the study area to resolve high-voltage concerns.

- The 2023 needs assessment also found that two 115 kV substations in downtown Boston have short-circuit concerns and a few other study area substations had limited short-circuit margin.

- The solutions study update focused on developing solutions for three study subareas: northern (New Hampshire border to Boston, including the suburbs north of Boston), central (downtown Boston 115 kV system and the suburbs west of Boston), and southern (suburbs south of Boston). One of the two solutions utilized only AC system upgrades (AC Plan) while the other solution included a HVDC submarine cable (HVDC Plan). The result of the development of these two plans is a set of common upgrades included in both plans, a set of upgrades unique to the AC Plan, and a set of upgrades unique to the HVDC Plan. Both plans meet the reliability needs of the area.

- The common solution for the northern, southern, and central areas have been identified and are described below. Note that these do not include the advanced projects included in the needs assessment base cases.

- The common transmission solution for the northern area includes the following elements (all in Massachusetts, except where indicated):

- Line reconductorings on the 115 kV network in the North Shore area:

- Y-151 Power St.–Dracut Junction (part of the line is in NH)

- M-139 Tewksbury–Billerica 115 kV

- F-158N Golden Hills–Maplewood

The common transmission solution for the central area includes the following upgrades (all in Massachusetts):

- New 115 kV lines, as follows:

  - From Sudbury to Hudson

  - From Mystic to Chelsea

- New autotransformer additions as follows:

  - 345/115 kV autotransformer at Woburn

  - 345/115 kV autotransformer at Mystic

- New capacitor additions as follows:

  - 36.7 MVAR capacitor at Sudbury 115 kV

  - 54 MVAR capacitor at Newton 115 kV

- Reconfiguration of the following substations that included breaker additions and line reterminations:

  - Waltham 115 kV substation

  - North Cambridge 115 kV substation

  - Kingston 115 kV substation

  - Woburn 345 kV substation

  - K Street 115 kV substation

- Separation of the following double-circuit tower instances:

  - X-24/E-157W (Millbury–Northboro Rd./Millbury–E. Main St.)

  - F-158N/Q-169 DCT instance (Wakefield–Maplewood/Wakefield–Lynn)

  - 240-510/110-522 DCT (Baker St.–Needham)

- Upgrades on the 69 kV network in the central area

X-24 line refurbishment: Millbury–Northboro Rd.

W23W: Northboro–Woodside

The common transmission solution for the southern area includes the following upgrade (all in Massachusetts):

A new 345 kV shunt reactor at Holbrook 345 kV substation

- A new 345 kV breaker at Stoughton 345 kV substation

- The AC Plan and the HVDC Plan each include a unique set of upgrades specific to each plan.

- The AC Plan includes two new 345 kV lines:

- A Scobie–Tewksbury 345 kV line

- A Wakefield–Woburn 345 kV underground line

In addition to the two 345 kV lines, a 115 kV cable will be installed in downtown Boston parallel to the existing 211-514 from Mystic to Woburn. Both cables will be operated as a single circuit. The plan includes several 115 kV reconductorings in the northern and western subareas. The short-circuit mitigation plan, as a part of the AC Plan, involved opening the terminals of four 115 kV cables in downtown Boston, which resulted in these cables being energized radially. Additionally, two 345 kV shunt reactors would be required to be installed at the Wakefield and Woburn substations to resolve the high-voltage issues observed at minimum load. A dynamic reactive device will also be required to be added in Maine to achieve acceptable stability performance.

- The HVDC Plan includes:

- A 520 MW HVDC cable between the Seabrook 345 kV station and the Mystic 115 kV station and an associated converter station at each location

- Reconductoring of the 345 kV 337 line between Sandy Pond and Tewksbury

- Along with this upgrade, the northern subarea requires some terminal equipment additions and replacements and an additional 115 kV reconductoring. The short-circuit mitigation plan as a part of the HVDC Plan involves a major reconfiguration of the Mystic 115 kV substation. The substation will be operated as two independent switchyards:

- One of the switchyards will consist of five 115 kV cables that connect Mystic to downtown Boston and include the interconnection point of the HVDC injection. The distribution transformers at Mystic will be connected to this switchyard.

- All other 115 kV equipment, including the 345/115 kV transformers, will be connected in a separate switchyard. These include the Mystic 115 kV generation and the three 115 kV cables between Mystic to the North Shore area.

- The ISO is reviewing the merits of the AC and HVDC plans, which includes an independent review of the cost of each alternative to ensure that the most cost-effective solution is selected for the Greater Boston area. The cost estimates submitted for all plans were presented at the June 2014 PAC meeting. The cost estimates are undergoing further review.

Berkshire County/Pittsfield area: The completed solutions study for this area describes the area’s final transmission solution, which consists of the upgrades listed below. An updated reassessment of the needs, accounting for updates to the load forecast and changes in resources and energy efficiency, has been completed, which shows that most of the needs existed before 2013 at the load levels of that year:

- Expand and reconfigure Northfield Mountain 345 kV substation, and install a 345/115 kV autotransformer

- Build a three-breaker ring-bus switching station in Erving adjacent to the A127/B128 (Harriman–Millbury/Harriman–Millbury) right-of-way

- Build a new 1.2 mile 115 kV single-circuit line connecting the new Northfield 345/115 kV autotransformer to the new Erving switching station

- Rebuild the 115 kV 1361 line (Montague–Cumberland)

- Loop the 115 kV A127 (Harriman–Millbury 115 kV) line into the new Erving switching station, and reconductor the A127 line from Erving to the Cabot tap (on the way to Harriman substation)

- Disconnect Montague from the 115 kV B128 line at Cabot Junction, and reconnect to the A127 line (Harriman–Millbury)

- Remove the sag limitation on the 115 kV 1421 and 1512 lines (Pleasant–Blandford–Granville Junction)

- Rebuild the 115 kV A127/Y177 double-circuit line from Montague to Cabot Junction on single-circuit structures

- Reconnect the Y177 line into the 3T/4T position at Montague substation

- Install 115 kV capacitors at Podick, Amherst, and Cumberland substations

- Install a bus-tie breaker between buses 1 and 2 at Harriman substation

- Replace five air-break disconnect switches on the A127E line between Erving and Barre

- The recently completed needs reassessment shows no further need for the following solution components:

- Reconductoring the 115 kV 1371 line (Woodland–Pleasant)

- Replacing the E131 115 kV breaker at Harriman substation

- In addition, the recently completed needs reassessment has shown the need to incorporate additional voltage control devices into the solutions proposed for this study area. The reassessment of the solutions study is underway and will specify the type and size of the needed voltage-control devices.

Massachusetts/Rhode Island—The needs assessment for the Southeast Massachusetts/Rhode Island study (the Eastern REMVEC study) is currently concluding, and the study is advancing into its solutions study phase. Past studies that included the Brayton Point plant have indicated a need to add transmission capacity to remove limits on moving power into and around the West Medway substation. However, with the upcoming retirement of Brayton Point station in 2017, the need for additional transmission capacity has been reevaluated. In addition, this study has reevaluated the need for portions of the Greater Rhode Island transmission upgrades.

The study has identified needs that require solutions to serve the broad southeast Massachusetts and Rhode Island load areas reliably. The solutions study will identify possible solution alternatives and provide recommendations for a preferred set of transmission upgrades for the area.

With the announcement of the Brayton Point retirement, a short-term study has been conducted to ensure that the SEMA/RI area can operate reliably in the absence of the station. A similar study was undertaken in 2010 when the Salem Harbor station announced its retirement. The transmission upgrades needed to address potential reliability concerns in the area due to the Brayton Point retirement are as follows:

- Reconductor the V148N line (Woonsocket–Washington)

- Increase the T175 transformer rating at West Farnum

- Increase the T3 transformer rating at Kent County

The solution to address the 1280 line (Whipple Junction–Mystic) and the 1870S line (Shunock–Wood River) thermal overloads requires further investigation and will be developed in the future.

Connecticut—A long-term reliability needs assessment for 2018 was completed for the Southwest Connecticut area, and solutions are being developed to address the criteria violations. The solutions analysis focused on developing solutions for five study subareas: Frost Bridge–Naugatuck Valley, Housatonic Valley/Norwalk–Plumtree, Bridgeport, New Haven–Southington, and Glenbrook–Stamford. The Glenbrook–South End cable and the Mill River–Quinnipiac 8300 line reconfiguration included in the New Haven area solution alternatives (see Section 5.4.2.3, Southwest Connecticut Advanced Solutions) were developed to address independent subarea needs. Other solution alternatives were developed to address interdependent subarea needs.

A new needs assessment and solutions study, referred to as the 2022 SWCT Needs Assessment and Solutions Study, was initiated to take into account the latest assumptions, changes in topology resulting from the approval of new projects and the results of the latest FCA, and the inclusion of energy efficiency beyond the latest FCA. The 2022 SWCT needs were first presented to the PAC in May 2013. Bridgeport Harbor 2 has already retired, and Norwalk Harbor station will retire by June 2017. As a result, the 2022 SWCT needs were reevaluated, and the needs assessment was presented to the PAC in February 2014. Needs were still present in all subareas with the exception of the Glenbrook–Stamford subarea. The advanced Glenbrook–South End cable mitigated all the violations found in the earlier needs assessment.

As part of the solution development, the two categories of solution were developed: “local” and “global.” As detailed below, local solutions located in each subarea were developed for each subarea listed below. In addition, a global solution, which spans the subareas of Frost Bridge–Naugatuck Valley and Housatonic Valley–Norwalk–Plumtree subareas, was created. The main feature of the global solution was a new line from Bates Rock to Bunker Hill, which required the rebuild of both terminal stations. Because of the excessive cost of the global solution, it is not the preferred alternative and is no longer being considered.

The major components of the preferred solutions for addressing the needs in the Frost Bridge–Naugatuck Valley subareas include the following components:

- Loop the 1570 line (Devon to Beacon Falls) in and out of the Pootatuck substation (formerly known as Shelton substation)

- Install two 115 kV capacitor banks at Ansonia substation

Expand Pootatuck substation to a four-breaker ring bus and install a 115 kV capacitor bank

Close the normally open breaker at Baldwin substation

Install a 115 kV capacitor bank at Oxford substation

Loop the 1990 line (Stevenson–Baldwin Street–Frost Bridge) in and out of the Bunker Hill substation

Rebuild Bunker Hill substation to a nine-breaker, breaker-and-a-half configuration

Reconductor the 1575 line from Bunker Hill to Baldwin Junction

The major components of the preferred solutions for addressing the needs in the Housatonic Valley/Norwalk/Plumtree subareas include a combination of the following components:

Reconductor the 1887 line between West Brookfield and West Brookfield Junction

Install two 14.4 MVAR capacitor banks at West Brookfield substation

Reduce the size of the capacitor at Rocky River substation from 25.2 MVAR to 14.4 MVAR

Relocate a 37.8 MVAR capacitor bank within the Stony Hill substation

Install one synchronous condenser at Stony Hill substation

Reconfigure the 1887 line into a three-terminal line (Plumtree–W. Brookfield–Shepaug)

Reconfigure the 1770 line into two two-terminal lines between Plumtree–Stony Hill and Stony Hill–Bates Rock

Reconductor a portion of the 1682 line from Wilton to Norwalk, and upgrade Wilton substation terminal equipment

Reconductor the 1470 line from Wilton to Ridgefield Junction and Ridgefield Junction to Peacable

Install a 115 kV breaker in series with the existing 29T breaker at Plumtree Substation

Install a new 115 kV line from Plumtree to Brookfield Junction

Relocate one existing capacitor bank from the 115 kV B bus to the 115 kV A bus at Plumtree substation

Upgrade the 1876 line terminal equipment at Newtown substation

The preferred solution for addressing the needs in the Bridgeport and New Haven areas include the following components:

- Upgrade the Baird 115 kV bus

- Install two 115 kV capacitor banks at Hawthorne

- Upgrade the 115 kV bus system and 15 disconnects to 63 kiloamperes (kA) interrupting capability at Pequonnock

- Rebuild the 8809A/8909B lines from Baird to Congress

- Install a series breaker at East Devon

- Remove the Sackett phase-angle regulator (PAR)

- Install a series reactor on the 1610 line (Southington–June–Mix Ave) and two 115 kV capacitor banks at Mix Avenue

- Rebuild the 88005A/89005B lines from Devon tie to Milvon

- Replace two 115 kV breakers at Mill River to address TRV overduty issues

- Upgrade the 1630 line (North Haven–Wallingford–Walrec) relay at North Haven

- Separate the 3827 (Beseck–East Devon)–1610 (Southington–June–Mix Ave) double-circuit towers

- Rebuild the 88006A/89006B lines from the Housatonic River Crossing to Barnum

- Rebulild the 88006A/88006B lines from Barnum to Baird

The recently completed needs assessment showed no further need for the relay upgrades at the June substation.

A SWCT solutions study report is being drafted. As part of the development of solutions in SWCT, the preferred solution for meeting short-circuit criteria at Pequonnock was to delay the circuit-breaker fault-clearing time to reduce the interrupt duty. The solution includes the complete replacement of the transmission control house and relays to incorporate the additional time delay in the tripping logic. With the upcoming retirement of Norwalk Harbor station and Bridgeport Harbor 2, the control house and new relays are no longer needed. However, the need persists to replace bus work and disconnects at the Pequonnock station to address short-circuit concerns.

Two other study efforts in Connecticut, evaluations of the Hartford and Middletown areas, have now been combined with the Greater Hartford/Central Connecticut study. Load-supply issues exist under certain dispatch and transfer conditions. Additionally, the Greater Hartford transmission system can experience flow-through issues when its 115 kV circuits are called on, under contingency conditions, to carry the power normally supplied via the 345 kV system. Both voltage and thermal issues have been identified in the Middletown area under future conditions when local generation is unavailable and when the Haddam 345/115 kV autotransformer is out of service.

The Greater Hartford and Central Connecticut study area consists of about 35% of Connecticut load and spans the central and northwestern portions of the state. The objective of the study was to determine the reliability needs for both serving local load in the area and reassessing the needs that had driven the Central Connecticut Reliability Plan component of NEEWS. The CCRP project consists of a new 345 kV line from North Bloomfield to Frost Bridge that crosses the western Connecticut import interface. The need for the project was based on thermal violations on the 345 kV lines that form this interface.

The study area consists of four subareas: Greater Hartford, including the Southington station; Manchester–Barbour Hill; Middletown; and northwestern Connecticut. The study area, in general, consists of several load pockets with limited generation fed by limited transmission. The loss of two or more transmission paths into these load pockets results in the thermal overloads on the remaining transmission paths and low voltages within the load pocket. The needs assessment for this study shows that system needs exist in all four subareas at 2013 load levels. The needs were attributed to load-serving issues and the need for increased import capability into western Connecticut. However, most of the 345 kV violations that drove the need for the CCRP project were no longer observed, and the project in its original form will no longer be required. The final needs report was posted in April 2014.

Solutions were developed for each subarea listed above. The major components of the preferred solutions for each subarea are highlighted below:

- Manchester–Barbour Hill

- Add a new 345/115 kV autotransformer at Barbour Hill

- Upgrade the 115 kV line from Manchester to Barbour Hill (1763)

- Add a series breaker at Manchester 345 kV switchyard

- Northwestern Connecticut

- Add a new 115 kV line from Frost Bridge to Campville substation

- Separate the 115 kV lines from Frost Bridge to Campville and from Thomaston to Campville DCT, and add a 115 kV breaker at Campville

- Upgrade terminal equipment on the 115 kV line between Chippen Hill and Lake Avenue Junction (1810-3)

- Reconductor the 115 kV line between Southington and Lake Avenue Junction (1810-1)

- Greater Hartford, including Southington

  - Replace the existing 3% series reactors on the 115 kV lines between Southington and Todd (1910) and between Southington and Canal (1950) with 5% series reactors

  - Replace the normally open 19T breaker at Southington with a 3% series reactor between Southington ring 1 and Southington ring 2 and associated substation upgrades

  - Add a breaker in series with breaker 5T at the Southington 345 kV switchyard

  - Add a new control house at Southington 115 kV substation

  - Add a new 115 kV underground cable from Newingtown to Southwest Hartford and associated terminal equipment, including a 2% reactor

  - Loop the 1779 line between South Meadow and Bloomfield into the Rood Avenue substation, and reconfigure the Rood Avenue substation

  - Reconfigure the Berlin 115 kV substation, including the addition of two 115 kV breakers and the relocation of a capacitor bank

  - Add a 115 kV 25.2 MVAR capacitor at Westside 115 kV substation

  - Reconductor the 115 kV line between Newington and Newington Tap (1783)

  - Separate the 115 kV DCT corresponding to the Bloomfield to South Meadow (1779) line and the Bloomfield to North Bloomfield (1777) line, and add a breaker at Bloomfield 115 kV substation

  - Install a 115 kV 3% reactor on the underground cable between South Meadow and Southwest Hartford (1704)

  - Separate the 115 kV DCT corresponding to the Bloomfield to North Bloomfield (1777) line and the North Bloomfield–Rood Avenue–Northwest Hartford (1751) line, and add a breaker at North Bloomfield 115 kV substation

- Middletown

  - Add a second 345/115 kV autotransformer at Haddam substation, and reconfigure the three- terminal 345 kV 348 line into 2 two-terminal lines

  - Upgrade terminal equipment on the 345 kV line between Haddam and Beseck (362)

  - Separate the 115 kV DCT corresponding to the Branford–Branford RR line (1537) and the Branford to North Haven (1655) line and add a series breaker at Branford 115 kV substation

  - Redesign the Green Hill 115 kV substation from a straight bus to a ring bus, and add a 37.8 MVAR capacitor bank

  - Upgrade terminal equipment on the Middletown to Dooley line (1050)

  - Upgrade terminal equipment on the Middletown to Portland line (1443)

- Add a 37.8 MVAR capacitor bank at Hopewell 115 kV substation

- Separate the 115 kV DCT corresponding to the Middletown–Pratt and Whitney line (1572) and the Middletown to Haddam (1620) line

A GHCC solutions study report is being drafted.

Finally, the eastern Connecticut area study is in progress. The eastern Connecticut area is defined from the east by the Connecticut and Rhode Island border, from the south by the Long Island Sound, from the west by the eastern boundary of the western Connecticut import interface, and from the north by the border between Connecticut and Massachusetts. The study area is served electrically from autotransformers at Killingly, Card, and Montville and by a 115 kV line from Rhode Island. The study evaluates the unavailability of the AES Thames generating unit among other issues. The needs assessment has been completed, and most of the needs are the result of the loss of the autotransformers at Card or Killingly or the 115 kV source from Rhode Island followed by another contingency. The needs assessment shows that most needs exist at 2013 load levels. The solution alternatives are being developed.

#### Southern New England Transmission System Projects

A number of transmission projects in various stages are underway in southern New England. Many factors complicate the system performance in southern New England, such as load levels, system transfers, and unit commitment. The projects identified for this area must function reliably under a wide variety of conditions, and their development must support the operation of the overall system.

NEEWS—The Rhode Island Reliability Project addresses the need for additional 345/115 kV transformation and contingency coverage in the Rhode Island area, and the Greater Springfield Reliability Project addresses various thermal overloads under forecasted normal conditions and significant thermal overloads and voltage problems under numerous contingencies. Both projects were completed in 2013.

The Interstate components of the IRP, expected to be in service by the end of 2015, consist of the following upgrades to address the need to transfer power into eastern New England, western New England, Connecticut, and Rhode Island:

- Build a new 345 kV line from Card to Lake Road stations (CT)

- Build a new 345 kV line from Lake Road station to West Farnum station (RI)

- Build a new 345 kV line from West Farnum station to Millbury 3 station (MA)

- Expand the Card, Lake Road, West Farnum, and Millbury 3 stations

- Reconductor the existing 345 kV line from West Farnum to Sherman Road stations (RI)

- Rebuild Sherman Road station

Webster–Harriman 115 kV Refurbishment (A127/B128)—A refurbishment has begun for the A127 and B128 115 kV lines that run westerly from the proximity of the Webster Street substation in Massachusetts to the Harriman substation in Vermont. This project currently is scheduled to be completed in 2015.

Central/Western Massachusetts Upgrades—Past studies developed a 10-year plan for central Massachusetts and portions of western Massachusetts. This plan calls for adding a second 230/115 kV autotransformer and replacing four 230 kV breakers at Bear Swamp, replacing a transformer at Pratts Junction and Carpenter Hill substations, adding a new 115 kV line from Millbury to Webster, and implementing several other 115 kV upgrades. Some of the upgrades have been placed in service, with the remaining scheduled through 2017.

Salem Harbor–Railyard Cable Replacement—The replacement of the underground cables between the Salem Harbor and Railyard substations is scheduled to be completed in 2016.

Auburn Reliability Project—Past studies of the area surrounding the Auburn Street substation in Massachusetts identified overloads of the existing 345/115 kV autotransformer and several 115 kV lines, voltage problems, and breaker overstresses. The solution to eliminate these reliability deficiencies includes rebuilding the 345 kV and 115 kV switchyards at the Auburn Street substation to accommodate new bay configurations, along with the installation of a second autotransformer and the replacement of a number of breakers. The reconductoring of the 115 kV Auburn Street–Parkview and Bridgewater–East Bridgewater lines has been completed. Additionally, a number of distribution substation changes are being discussed that could modify the original project and its subsequent cost. The Bridgewater–Easton 115 kV line (E1) will be extended to supply a new municipal substation in Mansfield. The new Avon substation will be constructed and tapped off the newly reconductored Auburn Street–Parkview line (A94). The addition of a second distribution transformer at Dupont requires associated terminal work. The completion of this project currently is scheduled for 2015.

Lower SEMA Short- and Long-Term Upgrades—Plans to improve system performance in the lower southeastern Massachusetts (LSM) area, which includes Cape Cod, were separated into two phases. Phase 1 included the projects that could be put in place in an expedited timeframe. Phase 2 includes those projects that would serve as the long-term solution for reliable supply but would require state siting hearings. The short-term upgrades were completed in 2009, and the long-term upgrades received siting approval on April 27, 2012.

The long-term plan, scheduled for a 2014 in-service date, includes adding a new 345 kV transmission line from the Carver substation to a new 345/115 kV substation. This new four-breaker ring-bus substation, which has been designated the West Barnstable substation, will be located west of the Barnstable substation adjacent to the 115 kV line right-of-way. The Carver–Bourne section of the 345 kV line is new construction, and the Bourne–Barnstable portion of the new 345 kV line will use an existing 115 kV line built to 345 kV standards. The 115 kV line (the Mashpee–Barnstable 115 line) will be tapped into the new substation. The plan also involves placing the existing 345 kV Cape Cod Canal crossing on separate towers and reconductoring the 115 kV D21 line between Bell Rock and High Hill.

Greater Rhode Island (Advanced NEEWS) Project—Reliability concerns with the 115 kV system in the Bridgewater–Somerset–Tiverton areas of southeastern Massachusetts and the adjoining area in Rhode Island had been identified previously. The solutions to these concerns were a group of upgrades that had been combined with the advanced Rhode Island upgrades (associated with NEEWS studies) to become what is now known as the Greater Rhode Island transmission reinforcements. The advanced NEEWS upgrades, the new Berry Street 345/115 kV substation (MA) and the expansion of the Kent County substation (RI) with an additional 345/115 kV autotransformer, have been placed in service in 2011. The proposed non-NEEWS GRI solutions in the Massachusetts area include, among other projects, the construction of new 115 kV transmission circuits between Brayton Point and Bell Rock substations. These currently are scheduled to be in service in 2018 and will be reexamined as part of the SEMA/RI (Eastern REMVEC) study (see above).

Southwest Connecticut Advanced Solutions—The advanced solutions for SWCT include the following elements:

- Reconfiguration of the 115 kV 8300 line from Mill River to Quinnipiac—The SWCT Needs Assessment analysis showed thermal issues unrelated to other needs in the New Haven area. The solution to mitigate the thermal issues is to install a new 115 kV overhead line from Mill River to Grand Avenue and to extend the existing 8300 line from Mill River into a new Grand Avenue substation bay. The project was completed in 2013.

- Northeast Utilities’ Glenbrook–South End 115 kV Cable Project—The SWCT Needs Assessment analysis showed thermal and voltage issues in the Stamford–Greenwich and Darien–Compo subareas due to line and cable outages followed by 115 kV stuck-breaker and DCT contingencies. The solution to mitigate these issues is to install a new 115 kV underground cable between the Glenbrook and South End substations. The project is expected to be completed by December 2014.

Greater Boston Advanced Solutions—The advanced solutions for Greater Boston, which are not in service and are not anticipated to be in service in 2014, include the following elements:

- Sudbury autotransformer and capacitor bank project—The Greater Boston Needs Assessment analysis showed thermal and voltage issues due to line outages followed by a second line outage. In the worst-case scenario, the entire Sudbury load pocket of 300 MW of load would be lost. The solution to mitigate these issues is to install a new 230/115 kV autotransformer, five new 230 kV gas-insulated breakers, five 115 kV air-insulated breakers, and a new 115 kV capacitor bank. The project is expected to be completed by December 2015.

- Addition of a third 115 kV line from West Walpole to Holbrook—The Greater Boston Needs Assessment analysis showed thermal issues due to line outages followed by a second facility outage. In the worst-case scenario, the loss of the 447-508 and 447-509 DCT (N-1 event) (West Walpole–Holbrook) resulted in the loss of over 300 MW. The solution to mitigate these issues is to install a third 115 kV line from West Walpole to Holbrook. The project is expected to be completed by 2016.

- Installation of a new 115 kV switching station in Sharon—Although a third 115 kV line is scheduled to be installed between West Walpole and Holbrook, the load (over 300 MW) in the area is still susceptible to being lost as a result of N-1-1 events. The solution to mitigate this issue is the installation of a new three-breaker switching station in Sharon. The project is expected to be completed by 2017.

- North Cambridge line and transformer terminal swaps—The Greater Boston Needs Assessment analysis showed thermal issues on the 329–530 or 329–531 lines as a result of N-1-1 events. The solution to mitigate this issue is to swap terminal locations of the 329–530 line and transformer #1 and to swap the terminal locations of the 329–531 line and transformer #4. The project is expected to be completed by 2016.

## Information on Critical Load Levels

The ISO has been improving the information provided to stakeholders, especially the required timing of transmission projects. The load level most often drives the need for transmission improvements under the assumptions used in each of the studies. The load level at which a system problem could occur, and therefore a solution would be needed, is referred to as the critical load level. From this critical load level, an approximate year of need can be developed. However, the year of need can change as the load forecast and other influences, such as energy efficiency, vary.

The ISO provides information on critical load levels in the needs assessment and solutions study for each portion of the region investigated. In the April 2012 update to the New Hampshire/Vermont Needs and Solutions Studies (see Section 5.4.1.2), critical load levels were provided, and virtually all upgrades are required at load levels that already have been surpassed. A similar assessment was performed for the Greater Boston area and the GHCC study. The results of this analysis also showed numerous system concerns for load levels that already have been surpassed. Almost all the critical load levels for the Pittsfield–Greenfield area study were surpassed before 2013.

## Transmission Improvements to Load and Generation Pockets Addressing
Reliability Issues

The performance of the transmission system is highly dependent on embedded generators operating to maintain reliability in several smaller areas of the system. Consistent with ISO operating requirements, the generators may be required to provide second-contingency protection or voltage support or to avoid overloads of transmission system elements. Reliability may be threatened when only a few generating units are available to provide system support, especially when considering normal levels of unplanned or scheduled outages of generators or transmission facilities. This transmission system dependence on local-area generating units typically can result in reliability payments associated with out-of-merit unit commitments. The total cost for these reliability payments are a small portion of the overall wholesale electricity market costs in New England of $8.82 billion in 2013.

Several areas currently depend on out-of-merit generating units to some degree to maintain reliability, or have been dependent on these units until recently. These areas and the status of transmission projects that either have reduced or eliminated the need to run units out of merit to respect reliability requirements, or are expected to do so when the projects are completed, are as follows:

- Maine—Generation is required for maintaining system reliability following second contingencies involving flows from New Hampshire to Maine. The MPRP project (see Sections 5.4.1.2 and 5.4.1.3) is expected to help reduce the requirement for running certain generators to support the transfers from New Hampshire to Maine. Net Commitment-Period Compensation (NCPC) charges in the Maine area were approximately $7.4 million, approximately 14% of the New England total. Some out-of-merit costs in this period were associated with maintaining transmission system security during MPRP construction.

- Rhode Island—Generation is required for maintaining system reliability following second contingencies associated with import concerns and also with local-area constraints. NCPC charges in the Rhode Island area were approximately $10.0 million, approximately 18% of the New England total. The Interstate Reliability Project portion of NEEWS (see Sections 5.4.2.2 and 5.4.2.3) is expected to reduce concerns associated with import constraints. The upcoming retirement of Brayton Point Station may have an impact on NCPC charges in this area, but the upgrades that the ongoing SEMA/RI assessments will identify are expected to reduce NCPC after they are placed in service.

- Massachusetts

- Boston area—NCPC for the Boston area was reduced by shunt reactor installations, which were completed in the 2009 to 2010 timeframe after the Stoughton Cables Project went into service (see Section 5.4.2.2). NCPC for this area totaled approximately $14.4 million for 2013, approximately 26% of the New England total. The upgrades being pursued as part of the Greater Boston projects are expected to further reduce NCPC after they are placed in service (see Sections 5.4.2.2 and 5.4.2.3).

- Southeastern Massachusetts—The completion of the short-term Lower SEMA project, coupled with the temporary operating measures put in place, resulted in NCPC payments in this area of approximately $6.4 million, approximately 12% of the New England total. The upgrades that the ongoing SEMA/RI assessments will identify are expected to further reduce NCPC after they are placed in service (see Sections 5.4.2.2).

- Western Massachusetts/Springfield area—A preferred solution for the Pittsfield–Greenfield area has been selected; however, some out-of-merit costs likely will continue until improvements are placed in service. Minimal out-of-merit costs in this area were associated with the construction of the GSRP component of NEEWS, which is now complete. This area accounted for approximately $15.9 million of the 2013 NCPC charges, approximately 29% of the New England total.

## Delist Bids, FCA #4 to FCA #8

As part of the FCM rules, the ISO reviews each delist bid to determine whether the capacity associated with the delist bid is needed for the reliability of the New England electric power system. Capacity determined not to be needed for reliability is allowed to delist.

For FCA #4, which was held in August 2010 for the 2013/2014 capacity commitment period, 281 delist bids were received, representing 2,410 MW. In accordance with Planning Procedure No. 10 (PP 10), Planning Procedure to Support the Forward Capacity Market, the ISO reviewed and analyzed these bids and determined that 587 MW, representing Salem Harbor units #3 and #4, and 604 MW, representing Vermont Yankee, were needed for reliability. In a December 16, 2010, order, FERC accepted the ISO’s determination. In May 2012, the ISO notified Entergy that Vermont Yankee is no longer needed for
the FCA #4 capacity commitment period. Refer to Sections 4.1.3.3, 4.2, and 5.4.1.2 for more information on VY.

In February 2011, a nonprice retirement request (see Section 5.4.2.2) was submitted for Salem Harbor units #1, #2, #3, and #4 beginning June 1, 2014. The ISO found no reliability concerns associated with the retirement of Salem units #1 and #2. However, in May 2011, the ISO determined that Salem Harbor units #3 and #4 were needed to ensure continued reliability of the system. Soon after the ISO’s determination was issued, the ISO was notified that Salem units #3 and #4 will be retired on June 1, 2014.

For FCA #5, which was held in June 2011 for the 2014/2015 capacity commitment period, 201 delist bids were received, representing 1,775 MW. In accordance with PP 10, the ISO reviewed and analyzed these bids and determined that only Vermont Yankee was needed for reliability. The ISO subsequently determined in November 2012 that Vermont Yankee was not needed for reliability for the FCA #5 period and accepted the delist bid.

FCA #6 was held in April 2012 for the 2015/2016 capacity commitment period. The ISO reviewed and analyzed 191 delist bids, representing 1,968 MW. Several delist bids representing 79 MW were needed for reliability in the NEMA/Boston capacity zone. Subsequently, in February 2013, the ISO accepted these delist bids on the basis of updated studies.

FCA #7 was held in February 2013 for the 2016/2017 capacity commitment period. The ISO reviewed and analyzed 268 delist bids, representing 1,560 MW. The ISO accepted all delist bids. However, price separation occurred between the NEMA/Boston area and the rest of New England. The addition of new market resources and the final transmission solution for Greater Boston is expected to mitigate this concern by increasing the ability of the transmission system to move power into the area.

FCA #8 was held in February 2014 for the 2017/2018 capacity commitment period. The ISO reviewed and analyzed 100 static delist bids, representing 4,170 MW. No delist bids were rejected to meet reliability requirements. In August 2013, Entergy announced the retirement of the Vermont Yankee nuclear plant (604 MW) and submitted a nonprice retirement request. On October 16, 2013, the ISO determined the resource was not needed for reliability. In late September/early October 2013, nearly 2,400 MW additionally requested to leave the market by submitting NPRRs, specifically, five resources representing 1,535 MW from the Brayton Point Station, three resources representing 342 MW from Norwalk Harbor Station, and 554 MW of demand-response resources. On December 20, 2013, the ISO issued the reliability determination for these resources. Only the Brayton Point Station #1–#4 generators were needed for reliability.

## Other Needed and Elective Transmission Upgrades

This section discusses Market-Efficiency-Related Transmission Upgrades. It also provides information on several transmission upgrades developed and paid for by generator developers. The transmission upgrades must meet reliability performance requirements.

### Needed Market-Efficiency-Related Transmission Upgrades

The purpose of and requirements for Market-Efficiency Transmission Upgrades are described in Section 5.2.2. However, market-efficiency benefits also may be associated with Reliability Transmission Upgrades, particularly when out-of-merit operating costs are reduced.

### Transmission Improvements to Mitigate Congestion

Recent experience has demonstrated that the regional transmission system has little congestion among the New England load zones relative to the Hub. The highest mean annual positive congestion costs were $0.10/MWh at both the BOSTON and RI RSP subareas. At approximately $175,000 in 2013, congestion costs remain low, and mitigation by additional transmission upgrades is not warranted. Planned Reliability Transmission Upgrades might reduce congestion costs further, as well as potentially reduce transmission system losses.

### Reliability Transmission Upgrade Improvements to Load and Generation Pockets

Transmission solutions continue to be put in place where proposed generating or demand resources have not relieved transmission system performance concerns. The ISO is studying many of these areas, and while transmission projects are still being planned for some areas, other areas already have projects under construction and in service to mitigate dependence on generating units. Reliability Transmission Upgrades were used to address these system performance concerns, which contributed to a substantial reduction in out-of-merit operating costs.

Generating units in load pockets may receive second-contingency or voltage-control payments for must-run situations. Table 5-3 shows the NCPC by type and year.

Table 5-3
Net Commitment-Period Compensation by Type and Year (Million $)

| Year | Second Contingency(a) | Voltage | Total |
| --- | --- | --- | --- |
| 2003(b) | 36.0 | 14.4 | 50.4 |
| 2004 | 43.9 | 68.0 | 111.9 |
| 2005 | 133.7 | 75.1 | 208.8 |
| 2006 | 179.9 | 19.0 | 198.9 |
| 2007 | 169.5 | 46.0 | 215.5 |
| 2008 | 182.5 | 29.4 | 211.9 |
| 2009 | 17.2 | 5.0 | 22.2 |
| 2010 | 3.9 | 5.1 | 9.0 |
| 2011 | 6.0 | 5.9 | 11.9 |
| 2012(c) | 8.7 | 14.9 | 23.6 |
| 2013(c) | 38.0 | 16.6 | 54.6 |

(a) 	NCPC for first-contingency commitment and distribution support is not included.

(b) 	NCPC under Standard Market Design began in March 2003.

(c) 	Source: ISO New England, 2013 Annual Markets Report, Table 2-20.

The 2009, 2010, 2011, and 2012 figures showed a significant decrease from the preceding years, averaging less than $17 million per year. While 2013 showed a modest upturn in charges, Section 5.6 describes ongoing studies and upcoming system upgrades expected to mitigate these charges. Therefore, the incentives are limited for pursuing transmission upgrades solely to reduce dependence on these generating units and improve the economic performance of the system.

### Required Generator-Interconnection-Related Upgrades

No significant transmission system upgrades resulted from the interconnection of generators. Most of the Generator-Interconnection-Related Upgrades are fairly local to the point of interconnection of the generator. The RSP Project List identifies the PTF upgrades (see Section 5.3).

### Elective Transmission Upgrades

A number of new Elective Transmission Upgrades have been added to the ISO Generator Interconnection Queue. Many of these are focused on delivering zero or low-carbon resources to New England. As of June 1, 2014, 20 projects are under study as Elective Transmission Upgrades:

- Two-terminal, HVDC line between Maine Yankee substation and South Boston, MA

- HVDC line between Orrington, ME, and Boston

- 345/230 kV AC line between Plattsburgh, NY, and Burlington, VT

- 345 kV tie line between Houlton, ME, and the Maine Electric Power Company (MEPCO) 345 kV tie

- 345 kV tie line between Bridgewater, ME, and MEPCO

- HVDC line connecting offshore wind to south of Boston or Cape Cod

- Keene Road export enhancement

- HVDC line between Québec and the 345 kV Coolidge substation in Vermont

- HVDC line between Québec and the 345 kV West Rutland substation in Vermont

- HVDC line between Québec and the 345 kV New Haven substation in Vermont

- HVDC line between New Brunswick and the 345 kV Wakefield substation in Massachusetts

- Transmission expansion in Coos County, NH

- Transmission expansion of the New Brunswick–New England interface

- HVDC line between Québec and the 345 kV Coolidge substation in Vermont (A second project for this upgrade is under study.)

- HVDC line between Québec and the 345 kV Mystic substation in Massachusetts

- HVDC line between Québec and the 115 kV Georgia substation in Vermont

- HVDC line between Québec and the 115 kV Williston substation in Vermont

- HVDC line between northern Maine and the 345 kV K Street substation in Massachusetts

- HVDC line between Québec and the 345 kV New Haven substation in Vermont

- AC line between northern Maine and the Keene Road substation in Maine

The Northern Pass Transmission (NPT) Project received Proposed Plan Application approval on December 31, 2013. This project includes several upgrades and system changes, as summarized below:

- Install a 1,200 MW nominal, HVDC converter terminal at a new 345 kV substation in Franklin, NH, and a 0/100 MVAR static VAR compensator (SVC).

- Install a new 345 kV AC transmission line (3132) from the Franklin converter terminal substation to the Deerfield 345 kV substation.

- Reconfigure the Deerfield 345 kV substation and add 200 MVAR of shunt capacitor banks and one 0/+400 MVAR SVC. The existing 345 kV AC transmission line (391) will be looped into the 345 kV Deerfield substation.

- Install 210 MVAR of 345 kV capacitor banks at the 345 kV Scobie Pond substation. In addition two new 345 kV circuit breakers will be installed in series with the existing circuit breakers.

- Upgrade the 345 kV 373 line from Deerfield to Scobie Pond.

- Increase the 326 line SPS summer thermal-mode setpoint.

## Summary

From 2002 to June 1, 2014, 11 major 345 kV transmission projects have been completed in five states, and one other has recently been approved. These projects reinforce critical load pockets, such as in Southwest Connecticut and Boston, and areas that have experienced significant load growth, such as northwest Vermont. These projects also include a new interconnection to New Brunswick, which increases the ability of New England to import power from Canada.

The MPUC has approved the siting of most of the component projects of the Maine Power Reliability Program, and many components are under construction. The MPRP will establish a second 345 kV line in the north from Orrington to Surowiec and will add new 345 kV lines in southern Maine, creating a third parallel path from Surowiec to Eliot (Three Rivers) in southern Maine. This program will reinforce and augment the 345/115 kV transformation capability in various load centers of Maine for greater reliability to area loads. These new paths provide basic infrastructure to increase the ability to move power into Maine from New Hampshire and improve the ability of the transmission system within Maine to move power into the load pockets as necessary. The studies necessary to evaluate any changes in transfer capability from Maine to New Hampshire were completed in 2012. To address potential system reliability concerns associated with the upcoming unavailability of Salem Harbor and the potential unavailability of Vermont Yankee, specific transmission upgrades have been advanced. For the retirement of the generation at Salem Harbor, 115 kV line reconductoring projects were completed in the North Shore area. For Vermont Yankee, upgrades at Flagg Pond have been installed to address potential thermal overloads if Vermont Yankee is unavailable.

The New England East–West Solution series of projects has been identified to improve system reliability. The updated review of the need for the Interstate Reliability Project component of NEEWS is complete, and the preferred solution is unchanged. A reevaluation of the Central Connecticut Reliability Project has been completed with the Greater Hartford/Central Connecticut study. The project has been replaced with a number of 115 kV upgrades, which address both local Hartford area concerns and issues associated with imports into western Connecticut.

Costs associated with second-contingency and voltage-control payments have been mitigated through transmission improvements. Additional transmission plans have been developed, which reduce the dependence on generating units needed for reliability. An example is the Lower SEMA projects, whereby short-term improvements already have reduced dependence on the Cape Cod Canal generating units; further long-term improvements will eliminate the need to commit generation for second-contingency protection.

From 2002 through June 2014, 559 projects have been put into service, with an investment totaling approximately $6.6 billion. Additional projects (proposed, planned, or under construction), totaling approximately $4.5 billion, are summarized in the RSP Project List, which is updated periodically.

Many new Elective Transmission Upgrades have been proposed, which focus on delivering zero or low-carbon resources to New England. As of June 1, 2014, 20 projects are under study as Elective Transmission Upgrades, and one has received its Proposed Plan Application approval.

All transmission projects are developed to meet the reliability requirements of the entire region and are fully coordinated regionally and interregionally. Most projects on the RSP Project List remain subject to regional cost allocation. With transmission expansion in the region, the ISO meets all required transmission planning requirements, and little congestion is currently evident on the system.

# Studies and Other Actions Supporting the Strategic Planning of the Region

New England has fuel diversity, certainty, and flexibility issues. The region relies heavily on natural-gas-fired capacity, and serious and growing reliability problems have emerged because of fuel constraints of the natural gas delivery system and both the cost and availability of liquefied natural gas (LNG). The lack of firm contracts for natural gas has limited the availability of the fuel and funding for natural gas infrastructure expansion, and the gas units with dual-fuel capability have not always been effective due to limited fuel storage and the extended time required to switch fuels. Infrequently operated and older oil and coal resources have shown diminished operating performance as well as limited energy production, with oil units experiencing issues with fuel availability, delivery, and other challenges caused by the sporadic operation of the units. New England also faces the retirement of non-gas-fired generation, which will likely increase the regional reliance on natural-gas-fired generation. In addition, the development of intermittent resources increases the need for system flexibility. RSP14 discusses these overarching and overlapping regional risks and the major actions the region is taking, including those through the ISO’s Strategic Planning Initiative.

The ISO and other entities have been conducting many studies to provide information and data to regional stakeholders on these broad planning issues facing the region, the extent of these issues, and potential solutions. Listed below and discussed in this section are some of the more specific topics analyzed to address the region’s strategic risks:

- Operating experience for the winter 2013/2014, which shows the effects of limited fuel supplies on electric energy production and the results of regional actions to address this issue

- The interaction between the natural gas and electric power systems, which quantify the need for improving fuel certainty to the region

- Environmental regulations, which potentially affect generating units

- The development of variable resources, which affects system operations and planning

- Economic impacts of developing market resources in specific load pockets, which provide information to resource developers and policy makers

- Improvements to the wholesale electricity markets and system operations and planning, which affect the reliable supply of electric energy to the region

## Capacity and Electric Energy Production in the Region by Fuel Type

New England’s capacity and electric energy production in 2013 indicates that the region is highly dependent on natural gas-fired generation and lacks a more balanced mix of oil, coal, nuclear, and hydro and other renewable resources. As shown in Figure 6-1, approximately 43.0% of the regional capacity in 2013 was natural-gas-fired generation. This is almost twice as large as oil-fired capacity, which was the next-largest type of generation resource in the region. Figure 6-1 also depicts the electric energy produced in the region for 2013. The electric energy produced by natural gas power plants was approximately 45% of the regional mix. Nuclear generation supplied approximately 33% of the electric energy, but each of the other types of generating resources produced less than 6.5%.

Figure 6-1: New England’s summer seasonal claimed capability and electric energy production by fuel type for 2013.

Note: The capacity and energy statistics illustrated in the figure exclude the capacity and energy associated with imports and behind-the-meter generation not registered in the region’s wholesale energy markets. In 2013, the NEL was 129,377 GWh, pumped storage consumed an additional of 1,624 GWh, and the net imports into the region were 18,961 GWh.

Sources: The capacity data are RSP13 data and the same as 2013 CELT Report data (http://www.iso-ne.com/static-assets/documents/trans/celt/report/2013/2013_celt_report.pdf). The energy data are based on the March 1, 2014, 90-day resettlement of total electric energy production for 2013.

The future fuel mix of the region will show continued dependence on natural-gas-fired generation and the addition of intermittent renewable resources. Recent FCM auction results have shown the retirement of coal- and oil-fired generators in the region and the loss of the Vermont Yankee nuclear plant. As additional generators retire, units in the ISO Generator Interconnection Queue, which primarily are natural-gas-fired generation and wind resources (see Section 4.5.2), will likely replace them. Further increases in the use of natural-gas-fired generation will likely occur, resulting from the loss of other types of generation subject to risks, such as nuclear and hydro units that may not be relicensed. The region also is beginning to experience the addition of wind-powered generation and photovoltaic (PV) resources, and future growth is expected.

Figure 6-2 shows the expected regional resource capacity mix for 2014, 2017, and 2023. As indicated, natural gas-fired generation in the capacity mix is expected to grow from 43% from summer 2014 to 52% in 2023. In addition, public policies are encouraging the development of distributed resources, such as distributed generation, active demand response, and energy efficiency.

Figure 6-2: Generating resource summer capability by fuel type based on the 2014 CELT Report and the interconnection queue (MW, %).

Note: The 2014 values reflect the seasonal claimed capability of generating resources in the 2014 CELT Report. The 2017 capacity reflects the qualified capacity of new resources cleared in the FCA #8 (net of nonprice retirements and nonprice retirement requests for coal, oil, nuclear, and a few NPRRs for hydro and natural gas resources). The 2017 capacity also reflects projects in the April 2014 ISO interconnection queue considered likely to develop. The 2023 capacity reflects the 2017 resources plus other resources proposed in the ISO queue as of April 2014. While not all resources in the ISO queue are expected to develop, the resources are representative of the types of resources that will likely develop in the region. The active resources in the queue consist primarily of natural gas and wind generating resources. The wind resources have been derated to reflect their on-peak ratings used in transmission planning studies (i.e., onshore wind generation is modeled at 5% of nameplate; offshore wind is modeled at 20% of nameplate). (See Section 7.1.6 for a discussion of interchange with neighboring regions.)

## Natural Gas and Oil Fuel-Certainty Issues for Power Generation

ISO New England has immediate and growing concerns about the availability and flexibility of generating resources—particularly natural gas and oil-fired resources—to reliably serve the daily, round-the-clock demands of electricity consumers in New England. These concerns have been documented through the ISO’s Strategic Planning Initiative and were highlighted in the winter 2013/2014 period. The electric power system is the largest consumer of natural gas in New England. This dependence on the natural-gas fuel-delivery system that has limited local storage, combined with the economic pressures experienced by gas- and oil-fired generating facilities to participate in the wholesale electricity markets while attempting to minimize operating costs, are causing persistent reliability concerns. These concerns, while possible year-round, are most acute during extended cold-weather periods when natural gas demand by LDCs is high. Cold-weather conditions and the subsequent heavy demand for natural gas also can lead to natural gas pipeline constraints when electrical imports from neighboring regions may not be as readily available.

Operating experience has demonstrated the region’s increased reliance on natural-gas-fired capacity, the system’s energy production limitations (e.g., through resource nonperformance and lack of flexibility), and the challenges of achieving greater fuel certainty. In winter 2013/2014, New England experienced constrained natural gas pipelines and low inventories of both oil and LNG, which required extended time to replenish. Colder New England temperatures, which have commonly occurred, and the subsequent increase in electricity demand and decrease in the availability of natural gas for electric power generators would have exacerbated the operating situation. Another issue during cold spells is that fuel oil inventories can be depleted rapidly for those units that have switched from burning natural gas to burning oil for economic reasons or because the ISO committed them for reliability reasons or to manage the inflexibility of fuel deliveries to gas-fired generators. Market rules that allow resources to constrain their operation when they have limited fuel have added to these concerns.

Most natural-gas-fired generators in New England have not made long-term financial commitments that would support the natural gas delivery infrastructure and storage facilities and, in turn, the reliability of the natural gas supply. The lack of alignment between the natural gas and wholesale electricity market days and the structural mismatch between the “24 x 7” demands of the electric power system and the less-liquid, overnight and weekend market for gas supply creates additional uncertainty regarding the commitment and dispatch of gas units during overnight and weekend hours. Other concerns have occurred when the interstate natural gas pipelines were being maintained or otherwise constrained, and when LNG inventories or injections into the interstate pipelines were low. LNG deliveries are subject to a worldwide market demand, increased costs stemming from shipping and processing, and weather-related interruptions.

This section discusses the region’s operational shortfalls and institutional barriers exacerbating fuel-certainty issues, relevant studies being conducted on the natural gas supply and delivery systems, and the market and operational solutions being implemented to address these issues.

### Natural Gas Infrastructure—Issues and Improvements

New England’s natural gas supply and delivery infrastructure, and its limitations, have become an area of focus for improving the region’s fuel availability. Six interstate pipelines presently serve New England:

- Four originate from the south and west:

  - Algonquin Gas Transmission (AGT) Pipeline

  - Tennessee Gas Pipeline (TGP)

  - Portland Natural Gas Transmission System (PNGTS)

  - Iroquois Gas Transmission System (IGTS)

- The Maritimes and Northeast (M&N) Pipeline originates in the Canadian Maritime provinces.

- The Granite State Gas Transmission System (GSGT) is in New Hampshire and does not bring gas from outside New England into New England.

Four LNG import terminals also serve New England, two onshore and two offshore:

- Everett LNG in Massachusetts and Canada’s Canaport LNG onshore terminals

- Neptune LNG and Northeast Gateway LNG offshore terminals

The Everett terminal is connected with the AGT and Tennessee Gas pipelines. The Canaport terminal sends natural gas through the M&N Pipeline, which has the option of delivering natural gas to New England from the offshore natural gas production fields of the Sable Offshore Energy Project (SOEP) and Deep Panuke in Nova Scotia, Canada. Figure 6-3 shows the major existing natural gas infrastructure serving New England.

Figure 6-3: Overview map of the natural gas infrastructure serving New England.

Source: ICF International (ICF)

Notes: Several pipelines shown in the map do not serve New England: Brunswick Pipeline is owned and operated by Emera New Brunswick. The Trans Québec and Maritimes Pipeline is owned by a subsidiary of Gaz Metro (Montreal, Québec) and is solely an intrastate distribution pipeline network serving northern Vermont.

As shown in Figure 6-4, the liquefied natural gas deliveries to LNG import terminals have declined substantially in recent years, as reported by the Energy Information Administration (EIA) of the US Department of Energy (DOE). ISO system operations forecasters also have observed this decline on the pipeline electronic bulletin boards. This has limited the availability of spot-market gas within the Northeast.

Figure 6-4: LNG sendout from Canaport LNG terminal/Maritime pipeline and Everett LNG terminal, November 2010 to May 2013 (MMcf/d).

Source: EIA, “High Prices Show Stresses in New England Natural Gas Delivery System,” article, ”Issues & Trends: Natural Gas,” webpage (February 7, 2014), http://www.eia.gov/naturalgas/issuesandtrends/deliverysystem/2013/.

While the interstate pipeline companies that serve the Northeast region have added numerous interconnects from the area’s large and small producers, and annual natural gas production volumes in the Northeast are forecasted to rise from 3.92 trillion cubic feet (Tcf) in 2013 to 6.66 Tcf in 2024, New England cannot access the full benefit of Marcellus shale production. Figure 6-5 shows existing pipeline capacity constraints leading into the region from the west and southwest, as well as recent regional pipeline capacity additions.

Figure 6-5: Northeast natural gas pipeline constraints (left) and recent pipeline-capacity additions, 2011 (right).

Source: EIA, “New Northeast Natural Gas Pipeline Capacity Comes On Line” (January 27, 2012), http://www.eia.gov/todayinenergy/detail.cfm?id=4750, and “New Pipeline Project Could Lower Natural Gas Transportation Costs to New York City” (July 3, 2012), articles, “Today in Energy,” webpage.

At present, of the 30 proposed pipeline-expansion projects under development across the Northeast, only the following six projects would specifically bring either new or incremental pipeline capacity and access to additional natural gas supplies to New England:

- Portland Natural Gas Transmission System’s Continent-to-Coast “C2C” project, combined with upstream expansion to provide more capacity on the TransCanada and Trans-Québec and Maritimes (TQM) pipelines could result in PNGTS’ total capacity of approximately 350 thousand dekatherms per day (MDth/d) by November 2016. No construction would be needed on the PNGTS system.

- Spectra Energy’s Algonquin Incremental Market (AIM) Project, with a projected in-service date of November 1, 2016, would expand the capacity of the existing Algonquin pipeline in southern New York, Connecticut, and Massachusetts, and increase New England’s pipeline capacity by 342 MDth/d.

- Kinder Morgan’s Connecticut Expansion Project, with a projected in-service date of November 2016, involves minor pipeline looping and increased compression primarily within Connecticut. This should provide Connecticut gas LDCs with access to another 72,100 dekatherms per day (Dth/d) of pipeline capacity with access to Marcellus production sources.

- Kinder Morgan’s Northeast Expansion Project, with an in-service date of November 1, 2018, involves the construction of approximately 179 miles of pipeline looping and new construction primarily within New York and Massachusetts. This could provide New England with access to Marcellus and other production sources.

- Iroquois Gas Transmission’s Wright Interconnection Project (WIP), near Wright, New York, in conjunction with the proposed Constitution Pipeline (from northeastern Pennsylvania to upstate New York) would provide additional access to Marcellus gas supplies up to 650 MDth/d. An early 2016 in-service date is projected.

- The Atlantic Bridge Project, a proposed expansion of the AGT and M&N pipeline systems, will connect abundant North American natural gas supplies with markets in the New England states and the Maritime provinces. Atlantic Bridge recently completed an open season for customers to submit requests for additional natural gas service with a target in-service date of November 2017.

As of the publication date, the ISO was not aware of any electric power generator within New England that has signed a firm contract for any portion of these regional upgrades.

Unlike the electric power industry, which builds infrastructure in anticipation of demand, interstate natural gas pipeline companies build or expand pipeline capacity using a business and regulatory model that requires gas shippers and customers to enter into long-term firm commitments before the infrastructure can be developed. Although the natural gas pipelines serving the region are at or near capacity, they will not be expanded until customers make firm commitments. In fact, FERC, which must approve interstate pipeline projects, bases its decision that a pipeline project is in the public convenience and a necessity in large part on the existence of firm contractual commitments.

The recent and planned expansion and other upgrades to the regional and interregional natural gas infrastructure provide initial steps for expanding access to natural gas sources to meet New England’s increasing demand for natural gas to generate electric power. More expansion will most likely be required, however.

### Overview of Winter 2013/2014 Operations

While the region already recognized several risks to the reliable operation of the regional power system, these risks became significantly more evident during 2013/2014 winter operations. System operators faced challenges due to the combination of high winter loads resulting from cold weather and the limited supply of natural gas and oil used to fuel generating units, which limited the energy production of these units. The sections that follow summarize the specifics of these winter events.

According to the EIA, winter temperatures across much of the eastern United States (east of the Rocky Mountains) were significantly colder in 2013/2014 compared with the same period in 2012/2013 (October to February). The Northeast was 13% colder than winter 2012/2013, which led to increased consumption and prices for the fuels used for space heating and electric energy production. While the overall winter seasonal temperatures in New England were close to the long-term average, several cold snaps were very severe.

New England experienced sustained, high natural gas prices during the winter, resulting in many oil-fired generators operating in economic merit. Although gas pipelines were often operating at their maximum levels to supply local distribution companies (LDCs) that in turn supply retail natural gas customers (with fuel for space heating), the ISO frequently operated with little gas-fired power generation. Because of the limitations of natural gas fuel for generators, the region relied on oil-fired generation for electric system reliability at a time when oil supply chains also became increasingly constrained. The oil steam units often ran at full output, even during the overnight hours, which reduced their oil inventories. Internal combustion units (ICUs) had extensive run times but limited onsite capabilities for oil storage.

With virtually all the natural gas- and oil-fired generators operating with limited fuel inventories and constrained energy-production capabilities, the reliable operation of the grid proved challenging for the ISO. During the coldest days, the ISO carried gas-fired units as reserves, but the increased dispatches to provide these reserves further stressed the gas pipelines for covering non-gas-fired contingencies. Carrying these reserves also increased out-of-market generation because certain gas units have high start-up and no-load costs, further exacerbated by high natural gas prices during this winter.

Figure 6-6 shows the monthly generation energy production by fuel type for winter 2013/2014. The ISO’s 2013/2014 Winter Reliability Solutions Program was instrumental in maintaining required fuel supplies during this time. The use of oil-fired generators was vitally important to the reliability of the ISO system, and units that had significant oil inventory at the beginning of winter showed the most reliable performance, although replenishing the oil midwinter proved difficult. Figure 6-7 shows the depletion of oil storage over winter 2013/2014 based on ISO surveys conducted the first of every month. The amount of oil storage is expressed as the number of 24-hour days the oil generators could run at the indicated megawatt output.

Figure 6-6: Generator energy production by fuel type for December 2013, and January, February, and March 2014.

Figure 6-7: Depletion of oil storage inventories at regional generation facilities.

Replenishing oil during cold weather is challenging for generating units. This was demonstrated by the difficulties with oil transportation and availability in New England and other regions during winter 2013/2014 and the environmental concerns about greater emissions from oil-fired plants compared with natural-gas-fired and other lower-emitting facilities (see Section 6.3). Barge transportation is difficult to secure and often slowed in the Northeast when winter weather is a concern (but also with the limited ability to transport cargo through shallow areas any time of the year). The limited availability of trucks and restrictions on the number of hours drivers are permitted to operate constrain the availability of trucking oil, especially no. 6 oil. Additionally, because no. 6 oil is a specialty oil primarily used by a limited number of electric power generators, the delivery of this oil must be planned in advance. Thus, no. 6 oil is less available during the winter months and not readily available on short notice.

The 2013/2014 Winter Reliability Solutions Program expired after winter 2013/2014. The ISO has initiated a modified program for winter 2014/2015, which could prove more challenging, given the retirement of the 619 MW Vermont Yankee nuclear unit by the end of 2014 (see Section 4.1.3.3). Actual operating conditions, however, will depend on a number of factors:

- The severity of the winter weather

- The 2014 year-end implementation of market rule changes on offer flexibility, which will allow market participants to change their energy market offers during the operating day and improve their ability to reflect in their offers the real-time costs of obtaining fuel

- FERC’s determination that generators have the obligation to procure fuel

- Additional ISO actions that would mitigate fuel supply risks

The region is in a precarious position for the next several winters as major resources other than gas continue to retire and longer-term proposed market enhancements and energy infrastructure improvements are years away.

#### Winter 2013/2014 Events

Two events during the winter 2013/2014 proved particularly challenging for ISO system operators. During December 2013, loads higher than forecasted coupled with other conditions led to the implementation of ISO operating procedures to address capacity deficiencies. In January 2014, ISO Operations faced difficulties during extensive resource outages resulting from weather, equipment failures, fuel constraints, and other reasons. Operating experience during these events showed the importance of communications between the ISO and the natural gas pipeline sector.

Winter Events—December 2013. On Saturday evening, December 14, 2013, the New England Balancing Authority Area implemented M/LCC #2, Abnormal Conditions Alert, and OP 4, Action during a Capacity Deficiency, to manage a reserve deficiency on the system. The principal contributing factors of the deficiency included net interchange curtailments from neighboring systems, loads running over the forecast, and unexpected generator outages and reductions of approximately 400 MW. The expected net deliveries for the peak hour were 3,277 MW, but the actual net deliveries were 2,591 MW because of the curtailments. For the first 16 hours on that Saturday, the actual load and forecasted load were very close, but during hour ending (HE) 5:00 p.m., the actual load started to diverge above the forecast value significantly, and ultimately it was 632 MW above the forecast.

Figure 6-8 provides an overview of the system’s hourly real-time LMPs for December 2013. The system experienced price variability because of the tight capacity situations and fuel limitations to natural-gas-fired units during the cold weather.

Figure 6-8: Hourly real-time locational marginal prices, December 1 to 31, 2013.

Notes: OP 4, Action 1, calls for the ISO to inform all resources that a capacity shortage exists. Action 2 calls for the ISO to dispatch real-time demand resources in the amount and location required. Action 5 requires the ISO to arrange to purchase available emergency capacity and energy, or energy only (if capacity is not available) from market participants or neighboring areas.

Winter Events—January 2014 (Polar Vortex). January 2, 3, 4, 7, and 8 were among New England’s coldest 5% of days in the last 20 years, with daily average temperatures between 5 and 12 degrees F (°F). The observed weather for Hartford and Boston for January 7 was colder than forecasted, and loads ran approximately 370 MW higher than expected.

Preparations made in advance of the cold snap enabled the ISO to manage the cold weather conditions and ensure that adequate resources were available to meet the load and operating-reserve requirements in a coordinated fashion. The ISO closely communicated its operations with neighboring ISOs/RTOs to confirm transmission interchange schedules.

System operation on January 7 and 8 was challenging because of forced outages and generator uncertainty in the ability to procure natural gas. The ISO was in close coordination with the Northeast Gas Association and the six interstate pipelines serving the region’s generating resources to discuss the cold weather conditions and areas of concern for both the gas and electric power industries. Most of the area pipelines were operating at or near capacity, with some registering record throughputs. However, a compressor failure at Delmont, PA, reduced gas nominations by 575,000 MMBtu on the Texas Eastern system, and the Iroquois system also was constrained. The interindustry communications were extremely beneficial to the ISO’s understanding of the pipeline system’s ability to support electric power system operations.

During the afternoon load pickup on January 7, the New England system experienced 15 forced generation outages, totaling approximately 1,500 MW of capacity. Six natural-gas fired generators on the New England system could not initially confirm their fuel arrangements for January 7 and 8, 2014. Several New England resources eventually responded (intraday) that fuel arrangements were in place, and 500 MW of emergency electric energy was then delivered to PJM through New York. This indicates the need for close coordination among various electric power system and natural gas system operators and the difficulty of arranging for gas during tight pipeline conditions.

Figure 6-9 compares the total megawatts generated during the January 7, 2014, evening peak with the total CSO for each fuel type. The figure shows that total natural gas generation during this time was under 50% of the total CSO for this fuel. Generation outages and reductions totaled approximately 3,100 MW on that day. Figure 6-10 shows the generation percentages by fuel type for this same day.

Figure 6-9: Generation by fuel type compared with CSOs, January 7, 2014, evening peak (MW).

Figure 6-10: Generation by fuel type, January 7, 2014, evening peak (%)

Notes: The pie chart shows the mix of generation by fuel type in New England during the evening peak load hour (HE 6:00 p.m.) of January 7, 2014, arranged by percentage of total generation. Natural gas includes generation fueled by LNG. The “Other” and “Wind” categories are each 1%.

#### Limited-Energy Generation Resources

The limited-energy generation (LEG) provisions of the market rules further reduce generator availability, essentially by allowing resources to limit their operation when they have limited fuel. During most of winter 2013/2014, all nonnuclear and non-coal-fired generators became LEGs, distorting market efficiency and resulting in unusual commitment and dispatch patterns. System operators experienced considerable difficulty in maintaining security-constrained economic dispatch when such a large portion of the generator fleet had a limited fuel inventory. Because of these tight supply conditions, over the past year, the ISO implemented operating procedures that prohibit cancelling the start up of natural-gas-fired generators (except for reliability reasons). This action improved system reliability but increased out-of-market costs from $20.4 million in December 2013 to $73.3 million in January 2014.

While system operators value information on whether a generator has a limited fuel supply, increases in the use of the LEG provisions by natural-gas-fired generators adds to the complexity of system operations, particularly during the types of operating conditions that occurred during winter 2013/2014.

#### Natural Gas Price Volatility

As shown in Figure 6-11, New England’s heavy reliance on natural gas-fired generation has resulted in natural gas fuel prices typically setting the price for wholesale electricity. Despite the increased use of oil-fired generators during January 2014, wholesale electricity prices reflected the volatility in natural gas fuel prices, as shown in Figure 6-12.

Figure 6-11: Real-time energy prices compared with regional natural gas prices ($/MWh; $/MMbtu).

Figure 6-12: Daily day-ahead and real-time ISO New England Hub prices and input fuel prices, January 1 to 31, 2014 ($/MWh; $/MMBtu).

Notes: Average price difference over this period (day ahead − real time) = $5.93.
Average price difference over this period (absolute value; ABS) (day ahead − real time) = $25.99.
Average percentage difference over this period ABS (day ahead – real time)/real-time average LMP = 16%.
Gas price is average of Massachusetts delivery points; no. 6 oil is New York spot price from the EIA.

Although the development of Marcellus Shale is a growing source of natural gas, pipeline limitations into New England typically cause price separation between New England and Marcellus supplies. During winter 2013/2014, however, natural gas prices in New England were often similar to the areas west of the region because of high demand across much of the Eastern Interconnection.

### Studies on Natural Gas Supply and Delivery to Power Generators

Several studies have quantified potential shortfalls in natural gas supply to electric power generators, and additional studies are underway. The ISO commissioned a white paper to quantify the extent of the regional fuel-diversity risk and assess the ability of the regional gas supply and delivery system to serve the gas demands of New England’s power supply. The ISO also commissioned a scenario analysis that identified potential shortfalls of natural gas supply to generating units. In addition, the Eastern Interconnection Planning Collaborative (EIPC) is conducting a study of the interactions between the natural gas and the electric power systems across the Eastern Interconnection (refer to Section 7.1.1).

#### Gas-Fired Power Generation in Eastern New York and its Impact on New England’s Gas Supplies

This ICF International white paper assesses the effects of new and existing sources of electric power demand located downstream of existing pipeline constraints in New York affecting both the New England natural gas and electric power system markets. The paper evaluates the methods by which similar power plants compete for both firm and interruptible natural gas transportation, which includes capacity released by firm contact holders (primarily LDCs). This paper also discusses the impacts to gas flows into and within New England from unauthorized overruns by gas consumers who take gas in excess of their scheduled volumes, upstream of or within New England. Additionally, the paper assesses the conflicting physical requirements and economic incentives that natural-gas-fired generators face as they compete within both the electric power and gas markets. The measures that ensure compliance with established pipeline operating tariffs and applicable ISO and RTO market and operating rules are also presented.

Regarding natural gas delivery into the region, the paper states that three of the six pipelines that serve New England (Algonquin, Iroquois, and Tennessee) also provide service to markets in New York. Several eastern New York gas-fired power generators are located upstream of New England generators but downstream of existing pipeline constraints. These New York generators compete for regional gas supply and transportation services with New England’s generators. The New York generators affect physical conditions that influence pipeline deliveries into and within New England.

As summarized in the white paper, consumers have benefitted from relatively low gas prices, but New England faces fuel supply challenges resulting from pipeline infrastructure constraints. One challenge is that FERC tariffs require pipeline developers to secure firm natural gas contracts to be able to recover the costs for improving the pipeline system (see Section 6.2.1), but electric power market participants in the Northeast have failed to make these firm contracts. Operational challenges year round, particularly during peak winter electric power demand periods, are likely to become more severe as gas consumption by electric power generating units continues to grow without these firm contracts or other firm fuel arrangements.

#### Assessment of New England’s Natural Gas Pipeline Capacity to Satisfy Short-Term and Near-Term Electric Generation Needs: Phase II

The ISO commissioned studies to quantify the extent of the regional fuel-diversity risk by assessing the ability of the regional gas supply and delivery system to serve the gas demands of the New England’s power supply. The Phase I study compared natural gas supply capabilities (contracted pipeline capacity, peak-shaving capabilities, and LNG import facilities) with projections of growth in peak winter day and summer day gas loads for the region through 2020. The Phase II study examined a variety of scenarios for New England gas supply and power sector demand. The four categories of scenarios considered retirements of non-gas-fired generators, growth of electrical energy efficiency, decreased LNG supply, and winter near-peak conditions.

The Phase II study shows that the New England natural gas market is likely to remain constrained through 2020. The winter near-peak analysis indicates that gas-supply deficits may occur on both peak days and on multiple high-demand days throughout the winter. Because of projected gas supplies, LDC demand, and electric generator gas demands, the electricity sector will most likely have a gas-supply deficit on 24 to 34 days per winter by 2019/2020.

The analysis considered increases in the currently contracted capacity on the interstate pipelines and the likely addition of 450 MMcf/d of new capacity by the end of 2016. The reduced consumption in the energy-efficiency cases was not sufficient to eliminate the projected supply deficits for winter peak days. Future imports of LNG into the region (Phase II decreased LNG) are likely to be well below the rated capacity of the import terminals. As in the Phase I study, neither Northeast Gateway nor Neptune are projected to receive any future LNG shipments.

#### Winter 2013/2014 Benchmark and Revised Projections for New England Natural Gas Supplies and Demand

This ICF study reevaluated the Phase II projections (discussed above) for New England natural gas supplies, firm LDC demand, and gas supplies remaining for electric power generators. The study used data for natural gas system performance during the winter of 2013/2014 (particularly during the polar vortex events; see Section 6.2.2.1), new projections for peak day winter and summer gas demand by electric power generators through 2020, and the results of FCA #8 (see Section 4.1.3). ICF then calculated potential gas-supply margins during peak winter and summer days through 2020. The revised projections for gas supplies available to electric power generation throughout the winter averaged nearly 500 MMcf/d lower than the original Phase II analysis throughout the study horizon.

Given the projected gas supplies, electric power system reliability during the winter months would be compromised by sustained cold weather. Assuming “extreme gas prices” (>$20/MMBtu, which would mean many oil units would be economically dispatched) and the same weather conditions as this past winter, winter peak-day gas supplies will be barely adequate or slightly in deficit through 2020. Outages of non-gas-fired capacity, such as a disruption to a nuclear unit, and contingency outages of natural gas supplies would result in a serious deficit in the gas supply in New England.

The LDC firm demand during summer is about 20% of the winter peak; thus, pipeline capacity is less likely to be constrained in the summer. However, gas supplies could be constrained even in summer because of high load conditions; reductions in pipeline capacity resulting from forced outages or maintenance conditions; and outages of non-gas-fired generators, such as nuclear units that would increase the need for natural gas-fired generators.

#### EIPC Gas-Electric System Interface Study

During its review of the draft Phase II EIPC Report, DOE identified a gap between the electric power and natural gas system infrastructures and anticipates greater reliance on natural gas for power generation. DOE requested that the EIPC evaluate the interactions between natural gas and electricity operations and planning, and during 2013, six of the EIPC planning authorities (ISO New England, NYISO, PJM, the Tennessee Valley Authority [TVA], the Midcontinent ISO [MISO], and the Independent Electricity System Operator [IESO] of Ontario), reconvened the Stakeholder Steering Committee (SSC). With the addition of a gas sector, the SSC developed a statement of work, solicited stakeholder comments, and issued a request for proposals (RFP) for competitive bids to perform the Gas-Electric System Interface Study technical analysis. The project was awarded to Levitan and Associates in October 2013.

The Gas-Electric System Interface Study consists of four principal tasks or “targets,” as follows:

- Target 1: Develop a baseline assessment, including descriptions of the natural gas-electric power system interfaces, interaction effects, and specific drivers of the pipeline/LDC planning processes

- Target 2: Evaluate the capability of the natural gas system to meet individual and aggregate core and noncore gas demand over a five- and 10-year horizon

- Target 3: Identify contingencies on the natural gas system that could adversely affect electric power system reliability, and vice versa

- Target 4: Review operational and planning issues, including fuel-assurance objectives, affecting the availability of dual-fuel-capable generation

The study schedule calls for conducting the bulk of the technical analysis during 2014. Draft reports will be provided for stakeholder input for each of the above targets. A draft report will be developed, posted for comments, revised, and finalized for submission to the DOE by mid-2015.

### Addressing Regional Fuel-Certainty Issues

The operating conditions during the past two winters have exposed the urgency of addressing the growing limitations in electric energy production due to fuel constraints. The region has begun to address the risks associated with fuel certainty for winter 2014/2015 as well as longer term. These measures include market redesign, electric power and gas sector coordination, policy developments, and other actions.

#### Market Solutions to Address Fuel Certainty

The ISO has been actively collaborating with stakeholders on comprehensive, near- and long-term rule changes across the region’s suite of energy, reserve, and capacity markets to address the challenges identified through the Strategic Planning Initiative. The changes share overriding goals for contributing to the reliable operation of the power system:

Enhancing market rules to improve the dispatch of resources

Improving market incentives for more reliable resource performance

Procuring sufficient resources to meet the region’s electricity needs

The ISO has been working on major rule changes to both the Day-Ahead Energy Market and Real-Time Energy Market to bolster the ISO’s ability to dispatch resources effectively, to improve how resources perform and respond to these dispatch instructions and schedules, and to ensure that prices accurately reflect current system conditions.

The challenges identified through the SPI have increased the need for flexible operations and reliable reserves and thus enhancements to the Forward Reserve Market and real-time reserve pricing (see Sections 4.3.2). The changes will improve the ability to manage intraday fuel-supply contingencies and produce prices and compensation more reflective of the true costs for these services.

The ISO also is working to enhance the FCM market. The goals of these improvements are to (1) provide sufficient incentives for generators to perform during stressed system conditions, (2) send price signals for new resources to locate in the areas of New England where new capacity is needed most, and (3) reduce the volatility of auction clearing prices as the market moves from periods of excess supply to periods when new resources are needed. Several market improvements are already in place and others are in various stages of development. Three key changes to the markets are energy market offer flexibility, FCM pay-for-performance (PFP), and the FCM sloped demand curve.

Energy Market Offer Flexibility. The ISO is implementing rule changes that allow generators to better reflect the real-time price of fuel in their supply offers. This will improve generators’ financial incentives to follow ISO dispatch instructions and will set more accurate prices in the energy market. A primary project on the ISO’s 2014 work plan, these changes require a significant effort to modify business processes and tools across many ISO departments, including system operations; market administration, settlements, and monitoring; and IT infrastructure and software. Starting in December 2014, market participants will be able to submit the following:

- Power supply offers that vary by hour in the Day-Ahead Energy Market, in contrast with current rules requiring the same offer for the entire operating day

- Timely changes to offers (until 30 minutes before the hour in which the offer applies) in the Real-Time Energy Market versus the current rules that restrict changes to a brief “reoffer period” the previous day

- Negative offers in day-ahead and real-time markets as low as –$150/MWh, which will provide an improved price signal for suppliers in the energy markets to reduce output or shutdown in anticipation of minimum generation conditions

FCM Pay-for-Performance. The ISO is developing a new “pay-for-performance” mechanism in the FCM, to be implemented on June 1, 2018, which will create stronger financial incentives for capacity suppliers to act as follows:

Perform when called on during periods of system stress: With PFP, a resource that underperforms will forfeit some or all capacity payments awarded in a Forward Capacity Auction; resources that perform in its place will get the payment instead. This means that the financial risk of nonperformance is placed on resource owners who have accepted capacity obligations; the capacity market price will not be affected during times of system stress, thus protecting consumers.

Make investments to ensure performance: Facing the risk of forfeiting capacity payments for underperformance—as well as the chance to receive more compensation for overperformance—resource owners will have the incentive to make investments that ensure their resource can perform. They have a variety of options, such as upgrading to dual-fuel capability, entering in short-notice or noninterruptible gas supply agreements, investing in new fast-start assets, or simply ensuring robust maintenance practices and adequate staffing. FCM rules will not dictate the technology or other means by which suppliers elect to do this but will merely create the incentive for resource owners to make cost-effective investments that meet the needs of operating a reliable system.

FCM Sloped Demand Curve. The Forward Capacity Auctions have always procured a fixed quantity of capacity regardless of the auction clearing price. In contrast, capacity auctions in other regions use a downward-sloping demand curve for capacity, in which the total quantity procured depends on the clearing price. Introducing a downward-sloping demand curve into New England’s FCA has the potential to accomplish the following:

Reduce price volatility over time, yielding smaller swings in capacity prices when the market moves from conditions of excess supply to periods when new capacity resources are needed, which may occur as aging plants retire

Allow the removal of other administrative pricing triggers that have proven difficult to implement

The ISO, joined by the NEPOOL Participants Committee, filed tariff changes, effective July 14, 2014, to incorporate a systemwide sloped demand curve and associated parameters for use in New England’s FCM. It will be used in the FCAs beginning February 2015 for FCA #9 and for the reconfigurations auctions.

#### Electric Power System and Natural Gas Sector Coordination

The implementation of operating procedures and improved communications between electric power and natural gas system operators over the past several years have improved the coordination between the natural gas supply and transportation systems and have prevented certain operational risks. The ISO continues to work with the natural gas industry to address the challenges of the increasing interdependency between the gas and electric power industries. Ways in which the gas sector could assist with reliability efforts include having gas suppliers provide generators with additional opportunities to obtain fuel outside normal business hours or having pipelines offer more flexible scheduling and additional services and provide real-time information on the status of the pipeline system. In addition, the ISO monitors planned upgrades in the natural gas infrastructure to maintain operational awareness of the natural gas system.

In November 2013, FERC issued regulations that allow the ISO and operators of the gas transmission system to share a broad range of nonpublic information to promote the reliability and integrity of each system. The ISO filed tariff revisions to permit the newly authorized communications in New England starting in early 2014. The changes are improving communications and information exchange between the control rooms of the gas and electricity networks for more informed decision making. Other ISO efforts include mining data from various sources to estimate the availability of natural gas for energy purposes, analyzing capacity scenarios across different seasons using information gathered from fuel surveys and pipelines, and establishing operating plans to deal with different system conditions.

#### Other Fuel-Certainty Improvements for Winter 2014/2015

The ISO is working with stakeholders to change the allocation of Net Commitment-Period Compensation. This is expected to improve the accuracy of day-ahead commitments by increasing incentives for load to bid into the day-ahead market. The ISO, in response to stakeholder comments, will not reallocate NCPC in the short term. However, the ISO plans to conduct a comprehensive evaluation of the NCPC cost-allocation methodology and anticipates that new recommendations will be discussed through the stakeholder process.

FERC has clarified the obligations of oil-fired generators to maintain sufficient inventory of fuel. Under good utility practice, cost-of-service oil-fired units must meet their load obligations. Capacity units also must meet strict performance requirements. Because oil cannot be procured in real time, sometimes taking days or months to replenish inventories, oil-fired generators must make arrangements in advance to ensure that they will have sufficient oil inventory for producing energy when dispatched during the winter. The ISO has worked with stakeholders on modifying the winter 2013/2014 fuel-reliability program. The modifications, submitted to and approved by FERC for a winter 2014/2015 reliability program, are intended to encourage generators to use dual-fuel capability and to compensate (1) active demand resources that provide 30-minute reserves (see Section 4.3), (2) participating oil generators for unused oil inventory, and (3) generators that contract for LNG to offset the risk of unused contract volumes.

#### Policy Developments

The New England governors recently expressed their collective perspective about the diversification of energy infrastructure in a statement entitled the “New England Governors’ Commitment to Regional Cooperation on Energy Infrastructure Issues,” dated December 2013. In addition, FERC is advancing better alignment of the natural gas and wholesale electricity markets.

NESCOE Projects. In furtherance of the New England states’ energy and environmental policy requirements and other statutory objectives (see Section 7.5), the New England states, through the New England States Committee on Energy (NESCOE) (see Section 7.3.1), have agreed that one or more requests for proposals will be issued to advance the development of transmission infrastructure. This infrastructure would enable the delivery of at least 1,200 MW, and as much as 3,600 MW, of “clean” energy into the New England electric power system from a combination of no- and low-carbon emissions resources. The states are also pursuing to increase the amount of firm pipeline capacity into New England of 1,000 MMcf/day above 2013 levels, or 600 MMcf/day (see Section 7.3.1), beyond what has already been announced for the AIM and Connecticut expansion projects (Section 6.2.1).

To assist in these efforts, NESCOE requested the ISO to provide the following to the states:

- Technical electrical system planning and associated support

- Support in developing and filing any tariff changes needed to advance the states’ objectives, including, as necessary, working together with the states and transmission owners responsible for cost-allocation filings with FERC

The New England states preliminarily agree, through NESCOE, that the recovery of the net cost of any such procurement of firm pipeline capacity should be collected regionally and that NESCOE should work with the ISO and NEPOOL to achieve this goal.

FERC NOPR to Better Align Natural Gas and Wholesale Electricity Markets. FERC recently issued a notice of proposed rulemaking (NOPR), proposing revisions to the natural gas operating day and scheduling practices used by interstate pipelines. The proposed revisions include starting the natural gas operating day earlier, moving the timely nomination cycle later, and increasing the number of intraday nomination opportunities. FERC simultaneously initiated parallel proceedings to further improve the coordination and scheduling of natural gas pipeline capacity with electricity markets.

## Impacts of Environmental Regulations on Generators and the Power System Overall

Compliance obligations for generators from existing and pending state, regional, and federal environmental requirements are likely to impose operational limits on new and existing generators but pose reduced retirement risks and lower adverse reliability impacts compared with earlier assessments. Federal air, water, and carbon standards could affect the economic performance of nuclear and fossil-fired (coal, oil, and natural gas) generators by increasing operating costs and imposing additional capital costs for needed controls or facility modifications. Other state and regional air, water, and carbon standards could require certain generators to reduce emissions further through the extended operation of pollution control devices, the use additional reagents, or the procurement of additional emissions allowances. Various elements of the power system are also subject to state, regional, federal, and international environmental land use, permitting, and siting regulations, many of which have protracted review periods that can complicate or delay planning, development, or the implementation of proposed transmission and generation improvements.

The US Environmental Protection Agency (EPA) is developing and implementing several air and water quality rules in the following areas that will have an impact on existing and new generators:

- Surface water withdrawals (for cooling water use and consumption)

- Wastewater discharges into surface water

- Mercury, acid gas, and other air toxic emissions

- Ozone (O3) transport and fine particulate matter (PM2.5) and sulfur dioxide (SO2) emissions

- Greenhouse gases (GHGs)/carbon emissions

Several New England states are developing or implementing air and water quality requirements for generators and GHG reduction targets under the Regional Greenhouse Gas Initiative (RGGI) or through Clean Energy Performance Standards. The Ozone Transport Commission, of which all New England states are members, also is developing model rules that states may adopt to reduce air pollution, and which may affect generators within and upwind of the region.

System reliability could suffer if the aggregate impact and timing of all these requirements limit generator energy production, reduce capacity output, or contribute to unit retirements. However, EPA has provided compliance options in several major recent rules, recognizing the reliability value that low-capacity fossil steam generators provide in maintaining system fuel diversity (see Section 6.2). Compliance with many of these requirements begins in 2015 and will continue through 2022.

### Emerging Impacts of Clean Water Act Regulations on the Region’s Generators

Major revisions of Clean Water Act standards, including the final § 316(b) Cooling Water Intake Rule and the proposed § 304 Effluent Limitation Guidelines (ELGs) for Electric Steam Generators, will require capital expenditures and increased overhead and maintenance costs for existing fossil and nuclear generators. New electric energy generation projects will likely require dry, hybrid, or closed-cycle cooling systems and the elimination of most wastewater discharges under zero-liquid discharge requirements. Figure 6-13 shows the number of cooling systems by primary energy source in 2012 nationwide.

Figure 6-13: Number of cooling systems in the United States by primary energy source, 2012.

Note: Of the 1,655 operable cooling systems in the United States, 875 (53%) reuse water through a cooling tower or a cooling pond, while 719 (43%) do not reuse water. The remaining systems are dry (56 systems) or hybrid (5 systems), which can switch between dry and some sort of wet cooling, depending on the temperature and availability of water.

Source: EIA, Form EIA-860, Annual Electric Generator Report.

#### Cooling Water Intake Rule Requirements

On August 15, 2014, EPA finalized the Clean Water Act 316(b) Cooling Water Intake Structure Rule requirements for the design and operation of cooling water intake structures at existing and new thermal power plants to mitigate the adverse impacts of these structures. Existing generators withdrawing at least 25% of their water from an adjacent water body exclusively for cooling purposes and have a design intake flow of greater than two million gallons per day (MGD) are required to reduce fish impingement (i.e., when fish or wildlife are trapped against the intake structure due to the velocity of a facility’s water withdrawals). Regulators will select from among seven mitigation technologies or operational options to satisfy the Clean Water Act 316(b) requirement for best technology available (BTA) for reducing impingement.

The agency and delegated states in New England will implement the latest Clean Water Act 316(b) rule, including design enhancements and operational requirements to reduce impingement mortality and new requirements to protect threatened and endangered species and critical habitats federally listed and designated under the US Endangered Species Act.Additional interim and permanent measures also may be required to protect shellfish and fragile species. EPA considered, but did not adopt, a specific BTA standard or technology or process categories for mitigating fish and wildlife mortalities caused by entrainment (i.e., when fish and wildlife are removed into the cooling system), instead opting to require site-specific entrainment BTA assessments. Generators withdrawing 125 MGD for once-through cooling systems for noncontact cooling on their steam cycles will need to assess the characteristics of their units’ entrainment.

Compliance with the impingement standards are due as soon as possible after final facility permits are issued with the new 316(b) entrainment requirements, with EPA anticipating most retrofits occurring between 2018 and 2022. Entrainment characterization studies are due 45 months after the effective date of the final rule (October 14, 2014). Using these studies, regulators will need to balance system reliability, the severity of the impacts to fish and wildlife populations, including protected and threatened species, and other factors, and they may require affected generator owners to replace existing cooling water intake structures or convert them to recirculating cooling systems. Unlike the proposal, which has an eight-year compliance window, the final rule does not specify deadlines for operators to conduct all necessary engineering, procurement, contracting, and construction activities for such retrofits.

As much as 12.1 gigawatts (GW) of existing fossil fuel and nuclear capacity in New England may need to modify their cooling water intake structures for impingement mitigation. EPA exempted existing generators with low capacity factors (i.e., below 8% averaged over two-year consecutive periods). Generators that meet the eligibility thresholds for these safe harbors are exempted from more intensive compliance obligations. A total of 5.6 GW of facilities with larger water withdrawals of once-through cooling systems will need to also prepare and submit entrainment characterization reports to regulators by 2018.

#### Changing Wastewater Discharge Requirements

To address changes in the toxicity of wastewater discharges from power plants, EPA proposed revisions to the Effluent Limitation Guidelines under the Clean Water Act, which would require many thermal generating stations to reduce or remove certain contaminants from their wastewater discharges beginning in 2017. EPA projects that up to 16 GW in the NPCC region may be affected. EPA agreed to finalize the ELGs for power plants by March 2015.

The proposed power plant ELGs present the largest uncertainty in the near term for those generators creating wastewater discharges of concern and operating air pollution control devices. These units mainly are coal-fired generators that use wet ash-management systems equipped with wet scrubbers.

### Clean Air Act Requirements and Regional and Federal Greenhouse Gas Regulations

Many Clean Air Act actions are ongoing that affect New England’s fossil-fuel power generators and the region’s air emissions. The Mercury and Air Toxics Standards (MATS) and other air-quality rules are being implemented, the impacts of which are shown by the trends in regional emissions. Regional and federal greenhouse gas regulations in various stages of implementation also will have a range of environmental and economic implications.

#### Implementation of Mercury and Air Toxics Standards

Recent revisions to air quality standards limiting ambient concentrations of ozone and its precursors—fine particulate matter and sulfur dioxide—will require additional reductions from larger fossil-fuel-fired generators, while technology-based performance standards affect other generators.

Approximately 7.9 GW of existing coal- and oil-fired capacity in the region are subject to EPA’s final Mercury and Air Toxics Standards. By April 2015, fossil steam generators greater than 25 MW in capacity must comply with the standard’s emissions limits for acid gases, toxic metals, and mercury on the basis of maximum achievable control technologies (MACT). However, most remaining coal-fired generators already are retrofitted with needed controls to comply with state air toxics regulations. In New England, an operator petitioned its state air quality regulator and was granted a one-year compliance extension request until April 2016 to complete the design and retrofit activities at two coal-fired generators.

Most remaining larger oil-fired generators in New England are only subject to de minimis work practice standards under MATS and are not required to add any emission control devices. Under MATS, oil-fired generators used as peaking units to help preserve system reliability and that maintain a capacity factor below 8% on two-year block average are exempt from otherwise applicable MATS emissions limits. Overall, less than 1 GW of affected fossil capacity in New England is considered at risk for retirement because of an inability to comply with MATS requirements.

#### Clean Air Act Regional Air Pollution Reduction

As much as 22 to 24 GW of existing fossil capacity in New England potentially will be affected by future state, regional, and federal rules implementing various air quality and performance standards required under the Clean Air Act for a range of air pollutants. State and federal air regulators are expected to address deteriorating air quality trends across southern New England (particularly due to ozone and fine particulate matter), possibly resulting in more stringent emissions limits for fossil generators. Ozone and fine particulate matter generated far upwind of New England has hampered considerable regulator efforts to improve local air quality. While EPA has repeatedly attempted to address the matter by enacting a number of rules to satisfy the “good neighbor” requirements of the Clean Air Act, it has only had mixed results, stemming from design flaws and litigation that limited their effects. These rules included the NOX “SIP Call,” the Clean Air Interstate Rule (CAIR), and the Cross-State Air Pollution Rule (CSAPR). However, on April 29, 2014, the Supreme Court overturned the CSAPR vacatur, deeming EPA’s finding and approach adopted in CSAPR acceptable (i.e., that emissions from upwind states contribute to downwind states' problems attaining federal air standards).

EPA must first address remaining administrative and litigation challenges to CSAPR and then decide whether to revise the rule. Another option would be for the agency to pursue a follow-up regional transported air pollution rule, which had been originally anticipated as a follow-up rule to CSAPR.

Such uncertainty makes it difficult to gauge the possible range of capital expenditures and annual compliance cost risks during the current planning period. This uncertainty already is having an impact on generators’ prices for future emissions allowances subject to the Clean Air Act Acid Rain Program and CAIR. In recent years, NOX and SO2 allowance prices have fallen to levels that make compliance costs essentially negligible, although historically, allowance costs comprised a significant part of operating costs for coal- and oil-fired generators. The ISO and generators use such pricing to gauge compliance costs and inform analyses that account for the timing, magnitude, and location of unit retirements that could result from generators’ opting not to comply with environmental regulations.

Other efforts have addressed air pollution transported into New England. On December 9, 2013, eight northeastern states petitioned the EPA, requesting it add nine Midwestern and southern states to the Ozone Transport Region (OTR). The petitioners, filing under a provision of the Clean Air Act (§ 176A), cited EPA modeling and their own analysis showing that emissions from the nine non-OTR states contribute significantly to violations of ozone standards in the eight northeastern states. The OTC also released a white paper in April 2014 proposing hourly NOX emission limits on all steam fossil, simple- and combined-cycle generators across the Northeast between May and September to reduce the severity of ozone pollution.

Under the federal Clean Air Act, states added to the OTR would have to use readily available control technologies and rely on cleaner fuels to generate power, consistent with the air pollution control efforts of the downwind states. If approved by the EPA, generators in New England may have an easier and less costly time meeting federal clean air standards resulting from reduced emissions from new upwind OTR states.

#### Regional Emissions Trends

Since 2001, the ISO has tracked the system emission rates and trends for NOX, SOX, and CO2 to help gauge the potential impact of future environmental regulations on the system and in response to a request from the states for emissions data. The ISO’s most recent air emissions report, the 2012 ISO New England Electric Generator Air Emissions Report, provides detailed historical trends and emissions rate data using a methodology developed with input from stakeholders.

Since 2001, the annual average NOX emission rate has decreased by 67%; SO2, by 92%; and CO2, by 23% (see Figure 6-14).

Figure 6-14: Annual average NOX, SO2 and CO2 emission rates, 2001 to 2012 (lb/MWh).

Note: These annual emission rates were calculated by dividing the total air emissions by the total generation from all units.

Source: 2012 ISO New England System Air Emissions Report.

The declines in NOX, SO2, and CO2 marginal emission rates on the system between 2001 and 2012 reflect declining capacity factors for coal- and oil-fired generators during a decade when natural-gas-fired combined-cycle and nuclear generators increased or maintained their share of the capacity factor. Total energy generation for 2012 was 3% lower than the total energy generation for 2011. This was reflected in decreases in the total system emissions for NOX by 19.7%; SO2, by 70.9%; and CO2, by 10.6%. The calculated system emission rates for 2012 are also lower than the 2011 values, and the NOX, SO2, and CO2 rates have decreased by 16.7%, 70.5%, and 7.8%, respectively. The decrease in average emission rates from 2001 to 2012 can be attributed to a decline in the cost of natural gas leading to the increased use of new, more efficient natural-gas-fired power plants and the decreased use of oil- and coal-fired power plants, plus the implementation of new emission controls on some of the region’s oil- and coal-fired units.

The increased use of non-gas-fired fossil generation, however, would increase emissions in the region. Given the increased use of oil-fired generators, especially during the winter months, annual emissions may increase in the short-term for New England.

#### Implications of Regional and Federal Greenhouse Gas Regulations

Fossil fuel-fired generators above 25 MW in New England are subject to the Regional Greenhouse Gas Initiative and to potential federal regulations of greenhouse gases.

RGGI states completed a comprehensive program review early in 2013 and issued program changes that RGGI states adopted for the succeeding compliance period, which began on January 1, 2014. As shown in Figure 6-15, the RGGI model rule revisions lower the overall CO2 budget (annual cap) to 91 million tons (mtons) annually beginning in 2014, with 2.5% reductions each year through 2020.

Figure 6-15: RGGI CO2 emissions cap compared with actual/projected emissions (2005 to 2020).

Notes: States participating in the current program include Maine, New Hampshire, Vermont, Massachusetts, Rhode Island, Connecticut, New York, Delaware, and Maryland. New Jersey withdrew from the RGGI program in 2012. As a result, the program cap and associated emissions declined starting in 2012.

Source: EIA, Lower Emissions Cap for Regional Greenhouse Gas Initiative Takes Effect in 2014, (February 3, 2014).

To account for the existing privately held CO2 allowances remaining from the first two compliance periods (2009 to 2011 and 2012 to 2013), in 2014, the RGGI program adjusted each state’s share of the regional CO2 budget by 100% of the private bank of allowances. This adjustment will be phased in between 2014 and 2020. Other RGGI program revisions include adding an allowance reserve to manage allowance market volatility (cost-containment reserve) and imposing an interim compliance deadline requiring affected generators to hold allowances covering at least 50% of their emissions during the first two years of each three-year compliance period. RGGI states expect that these and other minor technical amendments will promote a more robust and efficient allowance market.

On January 8, 2014, EPA reproposed a GHG New Source Performance Standard (NSPS) for new fossil-fuel-fired combustion generators greater than 25 MW, requiring them to meet an output-based standard of 1,000 pounds of CO2/MWh generated (lbs CO2/MWhgross). At the same time, the agency withdrew an earlier proposal published in April 2012. Average CO2 emission rates for pulverized coal steam-turbine generators range between 1,800 and 2,200 lb CO2/MWh, while many natural gas combined-cycle combustion turbines in New England emit below 950 lb/MWh of CO2 on average. In its Annual Energy Outlook 2014 (AEO 2014), the EIA anticipates only limited construction of new coal-fired generators, both for pulverized coal steam turbines and integrated gasification combined-cycle generators without carbon capture and storage. The EIA attributes this limitation to uncertainty about future carbon regulations, notwithstanding EPA’s flurry carbon rulemaking pursuant to the June 2, 2013, Presidential Memorandum.

EPA included new natural gas combined-cycle generators in the proposed GHG NSPS but excluded new natural gas simple-cycle combustion turbines from the standard, citing their lower GHG emissions when used primarily for peaking duty.

In June 2014, EPA proposed Carbon Emission Guidelines for existing fossil-fuel-fired power plants under Section 111(d) of the Clean Air Act. The proposed NSPS requires nationwide a 30% reduction in carbon emissions from affected fossil power plants from a 2005 baseline by 2030, with much of the reductions due by an interim deadline in 2020. Nationwide and in New England (shown below), the states have differing obligations for reducing carbon emissions by 2030, depending on their existing fossil generating capacity:

- New Hampshire (46.3%)

- Massachusetts (37.7%)

- Connecticut (29.4%)

- Rhode Island (13.8%)

- Maine (13.5%)

- Vermont (0%)

Once finalized (expected by June 2015), the NSPS requires states opting for individual compliance approaches to submit 111(d) SIPs by June 2016, while states participating in multistate 111(d) submittals have until June 2018 to submit joint plans. A wide range of approaches are expected in individual 111(d) SIP submittals; however, in New England, states are expected to seek approval for RGGI participation as satisfying all 111(d) obligations. Such an approach, in turn, would minimize the compliance obligations for existing fossil fuel generators in New England.

### Cost of Compliance with Environmental Regulations

The Strategic Planning Initiative identified as a near-term issue the retirement of generating units resulting from the costs to comply with environmental obligations. Most of the at-risk capacity faces compliance or retirement decisions later this decade and extending into the early part of the next decade, which is expected to affect positions in upcoming FCA auctions. The actual compliance timelines and costs will depend on the timing and substance of the final regulations and site-specific circumstances of the electric generating facilities. The ISO continues to identify such generators and study potential impacts.

## Update of Regional Nuclear Generation Licensing Renewals

New England has five nuclear generating generators: two in Waterford, Connecticut (Millstone), and one each in Seabrook, New Hampshire; Vernon, Vermont (Vermont Yankee); and Plymouth, Massachusetts (Pilgrim). Vermont Yankee notified the ISO on August 27, 2013, that it would cease commercial operation and negotiated an agreement with the State of Vermont to retire by the end of 2014 after exhausting its current fuel cycle. All remaining nuclear generators require an operating license, which is subject to renewals or extensions, as summarized in Table 6-1.

Table 6-1
New England Operating Nuclear Power Plants

| Unit Name | Operating (OP)/ Renewed License Date | License Expiration Date | Reactor Type | Electrical Output (MWe)(a) | Reactor Vendor/Type |
| --- | --- | --- | --- | --- | --- |
| Millstone 2 | September 26, 1975/ November 28, 2005 | July 31, 2035 | Pressurized water | 884 | Combustion Engineering (vendor) |
| Millstone 3 | January 31, 1986/ November 28, 2005 | November 25, 2045 | Pressurized water | 1,227 | Westinghouse/ four-loop |
| Pilgrim | June 8, 1972/ May 29, 2012 | June 8, 2032 | Boiling water | 685 | General Electric/ type 3 |
| Seabrook | OP: March 15, 1990 | March 15, 2030 | Pressurized water | 1,295 | Westinghouse/ four-loop |
| Vermont Yankee(b) | March 21, 1972/ March 21, 2012 | March 21, 2032 | Boiling water | 510 | General Electric/ type 4 |

        - “MWe” stands for electrical megawatts. Nameplate electrical output was obtained from the Nuclear Regulatory Commission’s (NRC) website, http://www.nrc.gov/info-finder/reactor/.

        - Entergy Nuclear Power Marketing intends to retire Vermont Yankee during 2014.

Operating license renewals for several reactors in the region cannot be finalized until the NRC revises two regulations (the Temporary Storage Rule and the Waste Confidence Decision Update) vacated by the DC Circuit Court of Appeals. The NRC expects to complete the replacement rulemaking for these matters no later than September 2014. In the meantime, licensing proceedings continue, and the ISO continues to monitor the proceedings for potential impacts.

The ISO is also tracking an EPA rulemaking updating radiation standards for commercial nuclear power plants, issued in 1977, triggered by advances in radiation exposure research and radiation risk assessment, the extension of nuclear reactor operating licenses, growing volumes of spent nuclear fuels onsite, and the risk of groundwater contamination. The ISO will track this rulemaking and assess its potential impact on the remaining nuclear generators in New England.

## Update on Hydroelectric Generation Relicensing

Most of the oldest generators on the system are hydroelectric generators, which include 1,374 MW, or 4.3%, of installed capacity available, and represent 7,177 GWh, or 6.4%, of all generation in 2013. In addition to providing capacity and electric energy, hydroelectric units traditionally have been well suited to provide regulation and reserves, but they may lose some of their ability to operate flexibly as part of their relicensing requirements.

The licenses for 1,945 MW of existing hydroelectric generators, including 1,720 MW of pumped-storage capacity, will expire between 2014 and 2022. FERC is pursuing an integrated relicensing review for several hydroelectric projects located on the Connecticut River with a completion deadline of April 2018 for all relicensing activities. Relicensing must take into consideration the requirements for adequately and equitably protecting and mitigating damage to fish and wildlife (and their habitats) and the recommendations of state and federal fish and wildlife agencies. The ISO is monitoring such proceedings to assess the impacts of operational restrictions, including the maintenance of minimum flows, on the ability of hydroelectric generators to offer regulation and reserve services.

Changes enacted in FERC’s hydroelectric generation licensing requirements of the Hydropower Regulatory Efficiency Act of 2013 are expected to have modest impacts on hydroelectric capacity in New England. The changes increase the small-hydro license exemption from 5 MW to 10 MW, remove conduit projects under 5 MW from FERC’s jurisdiction while preserving public review, and increase the FERC conduit license exemption to 40 MW for all projects.

## Wind and Photovoltaic Integration Activities

The integration of large amounts of intermittent resources poses new challenges to the electric power system. To address these challenges, the ISO has been conducting a number of studies, gathering operational data and observations, and participating in other projects.

### Potential System Impacts on Fossil Fuel Generators of Integrating Wind and Solar Resources

The US Department of Energy's National Renewable Energy Laboratory (NREL) released the second phase study examining the potential impacts of increasing wind and solar power generation on the operators of coal and gas plants in the West (including parts of Canada and Mexico). The report found that to accommodate higher amounts of wind and solar power on the electric grid, utilities will need to ramp up and ramp down (or start and stop) conventional generators more frequently than with less wind and solar on the grid. This report assessed various scenarios of wind and solar penetration and concluded that with about 25% of power supplied by wind and solar facilities in 2020, the projected cost savings resulting from the need for less fuel far outweighed the costs associated with increased ramping. Also, according to this report, overall emissions of SO2 and NOX would be reduced despite the impacts of increased ramping.

### Wind Forecasting and Dispatch

On January 15, 2014, the ISO began incorporating wind forecasting into ISO processes, scheduling, and dispatch services. (As of May 2013, the ISO has offered a preliminary informational wind power forecast.) In addition to the ISO’s use of the wind forecast, wind resources can download the forecast of expected output for their individual units, which can help them build a strategy for bidding in the Day-Ahead Energy Market. As part of phase 1 of this project, the ISO has also created displays that improve operators’ situational awareness and is now maintaining historical wind data for future use by the forecast service and in auditing and other analyses. The ISO will be working toward the full economic dispatch of wind resources, as well as publishing the aggregate wind energy forecast for the region in phase 2 of this project.

### Strategic Transmission Analyses—Wind Integration Study

ISO New England is conducting transmission system reliability assessments to identify the nature of the transmission system reinforcements necessary to integrate significant amounts of wind resources into the system. The most recent study effort focused on determining how much additional wind energy could be integrated in the State of Maine without major transmission system investment, particularly new lines. The first step was to examine the constraints of the local area transmission system, which are the types of constraints that have been the most restrictive in actual system operations. The assessment examined four specific regions:

- Keene Road region

- Bangor export region

- Wyman Hydro region

- Rumford export region

The assessments analyzed thermal, voltage, and stability-limit testing on local transmission interfaces. The second step of the analysis was to examine broader regional constraints to moving the aggregate wind and other resources from the four regions.

#### Study Approach

Base case power flow models were developed by adding representative stations for all wind resources in the ISO’s queue as of October 2013. The generators were interconnected with robust voltage control capability, which avoided the further significant depletion of system performance margins. Several load conditions were examined, and all wind resources within the area being investigated were increased from zero until a thermal limit was reached for transfer out of the region. System voltage and stability performance were then tested at these thermal limits to determine whether these limits were more constraining. The study identified the lower-cost improvements that increased the transfer limit for a region, such as adding reactive devices or series circuit breakers or rebuilding a short transmission line.

#### Results

The results showed that additional wind resources would displace traditional synchronous machine technology and the stability performance benefits of these types of machines. A dynamic device of up to 500 MVAR capability located in central Maine would likely be needed to integrate new wind resources effectively. At the same time, ensuring that these wind resources directly aid dynamic voltage control would improve the overall system performance during both normal and critical extreme contingencies.

The testing of the regional transmission interfaces identified the need for additional system reinforcements. These reinforcements include two 25 ohm thyristor-controlled series-compensation (TCSC) devices and 275 MVAR of 115 kV shunt capacitors in western and southern Maine. The TCSC devices are necessary to prevent system separation and the interruption of large amounts of resources following severe contingency events in southern New England. The shunt capacitors are required for voltage support in western and southern Maine.

Summary results for the four local regions are discussed below:

- Keene Road Region. The ability to add 85 MW to the existing 144 MW of wind capacity to this region was analyzed. The current system would probably not experience thermal violations at this generation level. A voltage stability issue would occur on the 115 kV path south of Keene Road due to local contingencies, and the performance of the system could be unacceptably degraded during extreme contingency conditions. Local constraints to existing and proposed generation could not likely be addressed without major transmission construction.

- Bangor Downeast Region. The ability to add 143 MW to the existing 34 MW of wind capacity to this area was analyzed. The 115 kV loop in this region is vulnerable to thermal overloads when a contingency occurs. Low 115 kV voltages also would occur at exports above approximately 130 MW, and the performance of the system could be unacceptably degraded during extreme contingency conditions.

Existing and proposed generation could be integrated with a few relatively small transmission upgrades. Study results are highly sensitive to the location of new plants and the electrical distance from the 115 kV loop. Voltage/transient stability problems are anticipated with amounts of generation greater than the 177 MW studied, and these voltage/stability constraints could not likely be addressed without major transmission construction.

- Wyman Hydro Region. The ability to integrate approximately 400 MW of wind capacity, including existing resources, in this region was analyzed. The current system would probably not experience significant thermal violations during the summer and winter but likely would experience thermal constraints during spring and fall when high hydro and wind conditions exist. Low 115 kV and 345 kV voltages could be experienced, and the performance of the BPS could be unacceptably degraded during extreme contingency conditions.

These local constraints to the added wind generation may be addressed without major transmission construction for up to approximately 400 MW (nameplate capability) of wind capacity, recognizing reasonably anticipated seasonal variations of plant output, provided that each new wind plant is interconnected with a physically and economically realistic amount of dynamic reactive compensation. Transmission improvements would include items such as the addition of series circuit breakers, the rebuilding of short sections of transmission lines, and the addition of reactive devices. This analysis did not address constraints that exist as a result of the major regional transmission interfaces.

- Rumford Region. The ability to add 130 MW of wind capacity to this area was analyzed. No thermal limitations would be expected at this generation level. Low 115 kV and 345 kV voltages could be experienced for normal design contingencies, and the performance of the system could be unacceptably degraded during extreme contingency conditions.

Upgrades would be needed to integrate existing and proposed generation. Local constraints could be addressed without major transmission line construction. System performance is interdependent with the Wyman Hydro region, and the transmission upgrades indicated for this region would also address constraints for Rumford region’s generators. This analysis does not indicate the extent to which generation could be added before minor or major transmission construction would become necessary. Again, this analysis did not address constraints that might exist due to the major regional transmission interfaces.

#### Conclusions

The Strategic Transmission Analysis examined the integration of approximately 1,100 MW of wind resources in Maine that could be accommodated without major new transmission lines. Transmission system improvements are necessary to address a combination of local and regional transmission constraints. Additional wind resources planned for the Wyman Hydro and Rumford regions could likely be accommodated without a major new transmission line to the local regions. However, the Keene Road and Bangor regions cannot support much additional wind capacity beyond the amount studied without major new transmission facilities. The addition of generation to the Aroostook region will require a new major transmission facility.

## Large-Scale Adoption of Photovoltaic Resources and Other Distributed Generation Resources

New England has witnessed significant growth in the development of solar photovoltaic resources over the past few years, and continued growth of PV is anticipated (see Section 3.4). PV installations not counted as ISO resources reduce the summer peak load, and while the technology holds promise as a nonemitting source of electric energy, it poses many challenges.

Regional PV installations are predominantly small (i.e., less than 10 MW) and state-jurisdictionally interconnected to the distribution system. State policies largely influence the spatial distribution of PV, such that states with policies more supportive of PV (e.g., Massachusetts) are experiencing the most growth of the resource. Existing amounts of PV have not caused noticeable effects on system operation, but impacts are anticipated as penetrations grow. To examine and prepare for the potential effects of large-scale PV development in the region, the ISO has engaged in the initiatives summarized below.

### Operational Solar Forecasting

Given that PV will predominantly consist of relatively small projects interconnected to the distribution system—that the regional system operator can neither observe or dispatch—these projects are effectively a weather-dependent modifier of system load. As penetrations continue to grow and displace energy production from other resources, the weather-influencing PV power production will introduce increased variability and uncertainty to the system and eventually will have an impact on system operations (e.g., result in the need for increased reserve, regulation, and ramping). As such, new forecasting techniques eventually will be required to account for PV generation appropriately.

In early 2013, the ISO began working on a three-year, DOE-funded project to improve the state of the science of solar forecasting. The results of this project will assist the ISO in developing a centralized solar forecasting system that eventually will be required to support the efficient and reliable integration of increasing amounts of PV. In the interim, the ISO is examining internal methods to improve its operational forecasts using artificial neural-network calculations.

### PV and Long-Term Planning

Long-term system planners consider PV in one of two ways. First, capacity supply obligations associated with PV projects that clear in the FCM can satisfy the Installed Capacity Requirement (see Section 4.1.1). Second, energy production or load reductions from operating PV assets are embedded in the historic loads used to develop the ISO’s 10-year load forecast, which in turn are used in planning studies (such as the ICR calculation, transmission planning studies, and economic studies). In fall 2013, the ISO initiated a stakeholder process to develop a long-term forecast of PV that accounts for the current and future growth of PV (see Section 3.4). The ISO and stakeholders are discussing the use of the PV forecast in long-term transmission planning by 2015, and economic studies already consider the PV forecast. In 2015, the ISO will evaluate the use of the PV forecast in other planning studies.

### Potential Reliability Impacts of PV

Because of the differences between the state-jurisdictional interconnection standards that apply to most PV resources and the FERC-jurisdictional standards that apply to larger, conventional generators, PV exhibits different electrical characteristics during system conditions typical of grid disturbances (e.g., low-voltage conditions during an unexpected outage of a large generator or transmission facility). The ISO is participating in a DOE project evaluating the potential reliability impacts of large amounts of distributed generation, such as PV.

The ISO asked the region’s utilities about their interconnection standards, and the responses indicated that most PV meets the existing IEEE 1547 standards. These standards were designed for relatively small penetrations of DG and do not require PV resources to be able to “ride through” a fault on the transmission system.

A high-level screening conducted by the ISO showed the potential loss of PV resulting from faults on the transmission system. The following maps in Figure 6-16, of Connecticut (left) and Massachusetts (right), show the areas where PV resources are likely to trip off line because of low voltage in the event of a fault on the 345 kV transmission system. This could result in thermal or stability problems and could cause the need for additional transmission upgrades. As PV penetrations grow, the severity of this potential problem will also grow.

Figure 6-16: Areas (in blue), in Connecticut (left) and Massachusetts (right), where PV resources are likely to trip off line because of low voltage in the event of a fault on the 345 kV transmission system.

Note: The key refers to per-unit voltage.

A sensitivity analysis also was conducted, which indicates that low voltage will be more widespread when local generation is not operating, for example, on a spring day with light load and high wind and solar generation.

The ISO is working with the New England states, distribution utilities, and IEEE and other international experts to ensure that the future interconnection standards for PV (and other inverter-interfaced DG resources) better coordinate with broader system reliability requirements. The ISO will participate in the revision of the IEEE standard with the aim of improving the coordination of distribution system needs and transmission system performance requirements.

The ISO also will continue to actively track the growth of PV in the region and evaluate its potential impacts on the efficient administration of wholesale electricity markets and the reliable operation and planning of the region’s electric power system. Because many other regions of North America also are witnessing the large-scale adoption of PV, the ISO also is engaging with other ISO/RTOs to share relevant methods and experience.

## Economic Performance of the System and Other Studies

Economic studies of various system-expansion scenarios have used metrics such as potential production costs, transmission congestion, and a number of others to suggest the most economical locations for resource development and the least economical locations for resource retirements. Other economic studies are showing the effects of possible new imports from Canada.

### Economic Studies

The 2011, 2012, and 2013 Economic Studies analyzed several of the strategic issues the region is addressing. The 2011 Economic Study examined the effects of integrating varying amounts of wind on production costs, load-serving entity (LSE) expenses, and emissions, as well as the need for transmission development, to enable wind resources to serve the region’s load centers. The 2012 Economic Study highlighted the least suitable locations for unit retirements and the most suitable locations for developing different resources without causing congestion. The study showed the effects of using various amounts of energy efficiency and low-emitting resources, including renewable energy. The 2013 Economic Study, still in draft form, examined the economic and environmental effects of increasing the acceptable loss-of-source (LOS) limits in New England.

The 2011 and 2012 studies with similar objectives showed several key results: Accessing the onshore wind energy located in northern New England remote from load centers will require transmission expansion. Replacing older high-emitting coal- and oil-fired units with cleaner-burning natural gas generation will decrease environmental emissions but increase New England’s dependence on natural gas and put additional demands on the natural gas infrastructure. The addition of resources with low energy production costs decreases electric energy expenses for LSEs but also decreases energy market revenues to other resources, which may then require increases in other revenue sources for these resources to remain economically viable.

In general, the results of the 2011 Economic Study and its follow-up analysis using GridView were in agreement. Highlights of these results are as follows:

- Transmission system limitations would not bottle in significant amounts of wind energy if up to 600 MW of wind resources were added in the Rumford area of Maine. However, the Wyman/Bigelow area, also in Maine, would become export constrained with 600 MW of wind development.

- The Surowiec South interface likely could limit wind production in north–central Maine, but the interaction of wind generation with the existing resources requires further investigation.

- Northern New Hampshire would be able to accommodate approximately 150 MW of wind without the need for major transmission upgrades to alleviate significant levels of congestion.

- SEMA/RI would be able to accommodate much more wind generation than the SEMA/RI wind resources currently in the interconnection queue likely would produce.

Additionally, the results show decreased systemwide emissions and natural gas consumption because the generation from wind resources displaces production from generating units burning coal, oil, and mostly natural gas.

The 2012 Economic Study showed the most suitable locations for developing various types of resources without causing congestion, including baseload, wind, photovoltaic, and energy efficiency, among other resource types. The study also showed the least suitable locations for resource retirements. The study compared a “business-as-usual” scenario of currently obligated and envisioned FCM resource additions with the effects of increases and decreases in several resource types. These types include active demand resources; energy efficiency; a mix of renewable resources based on the ISO Generator Interconnection Queue; “behind-the-meter,” distributed generators; and efficient natural gas, combined-cycle units. In addition to the typical metrics the ISO has provided in past economic studies (e.g., production costs, LSE energy expenses, and congestion), the simulation results showed where the system could have potential transmission bottlenecks from changes in resources in various locations and the effects of relieving these transmission constraints.

In general, the 2012 Economic Study confirmed that developing resources with low production costs near load centers reduce systemwide production costs, LSE energy expenses, and congestion. Developing resources remote from the load centers, such as northern Maine, could be subject to congestion. Retiring resources near load centers had more of an adverse effect on system performance than retiring resources in generation-rich areas remote from load centers, such as northern Maine.

The 2012 Economic Study also analyzed specific scenarios of resource mixes. The addition of resources with low or no fuel costs, such as combinations of efficient natural-gas-fired generators, wind, photovoltaic, energy efficiency, and demand response, showed reductions in the systemwide production cost and total LSE energy expenses. The study showed the estimated supportable $/kW-year capital costs plus technology costs for each type of resource based on its revenues from the electric energy markets. These revenues, however, were insufficient to support the postulated resources’ annual carrying charges, suggesting that other sources of revenue would be required to support the resource additions. Possible sources of revenues could be other wholesale electricity markets, such as the FCM and FRM, as well as other incentives, such as production tax credits.

The ISO is currently completing an economic study in response to a stakeholder request received in 2013. This study, scheduled for completion in the second half of 2014, is examining the economic and environmental effects of increasing the largest loss-of-source contingency allowed in New England resulting from an increase in needed operating reserves. The study assumes that both NYISO and PJM could accommodate an LOS contingency up to 2,000 MW. The study considers scenarios of imports over HQ Phase II that varied several parameters, such as the energy profile (i.e., import transfer levels, dispatch price, and hourly import schedules) and the modeling of operating reserves. As with other economic studies, the results show various metrics, such as the systemwide production costs, load-serving entity energy costs, LMPs, and emissions. The study included the following conclusions for when the HQ Phase II import level increases and the resource mix is assumed not to change:

- Systemwide production costs may increase or decrease, depending on the HQ Phase II import profile, reserve requirement assumptions, and the valuation of the energy at the point of interconnection (i.e., the LMP).

- Unit commitment costs and “make-whole” NCPC expenses increase.

- Load-serving entity energy expenses decrease.

- System LMPs decrease.

- SO2, NOX, and CO2 emissions may increase or decrease, depending on the HQ Phase II import profile and reserve requirement assumptions.

The ISO will not perform an economic study for 2014 because it did not receive any requests for one or propose one. However, it will be updating the production cost database and performing other studies. As may be required, the PAC will be kept advised of these studies.

### Generic Capital Costs of New Supply Resources

The comparison of the energy market revenues with the annual revenue requirements (also called annual carrying charges) provides some relative measures of the economic viability of different resource types and how these measures change under various scenarios. Each resource type’s annual fixed costs include its capital, operations, and maintenance costs. These fixed costs can be calculated from estimates of annual carrying charges derived from representative capital costs for each resource type. These typically are 15% to 25% of the capital costs.

In support of the economic studies, a 2014 update of generic capital costs for new resources was developed, as shown in Table 6-2. The focus of this update on capital costs was on the resource technologies in the ISO Generator Interconnection Queue and those participating in the FCM. The updated plant costs are from the EIA, the Electric Power Research Institute (EPRI), and the Brattle Group.

Table 6-2 
Generic Capital Costs of New Supply-Side Resources

| Technology Type(a) | Plant Size(b) (MW) | Heat Rate(b) (Btu/kWh) | Total Plant Cost(b) ($/kW) |
| --- | --- | --- | --- |
| Advanced combined cycle (CC) | 340–400 | 6,430–7,525 | 1,025–2,095 |
| Advanced gas turbine (GT) | 190–210 | 9,130–9,750 | 675–1,260 |
| Biomass | 20–100 | 12,350–13,500 | 3,600–8,180 |
| Conventional CC | 550–730 | 7,000–7,525 | 820–1,150 |
| Conventional GT | 85–420 | 10,580–10,850 | 640–975 |
| Natural gas fuel cells | 10 | 9,500 | 7,110 |
| Offshore wind | 200–400 | N/A | 3,100–6,230 |
| Onshore wind | 50–200 | N/A | 1,750–2,400 |
| Solar photovoltaic | 5–150 | N/A | 2,000–4,185 |

        - Technology types in the queue as of April 1, 2014.

(b) Additional information about these data is available in the ISO PAC presentation, Generic Capital Costs of Supply-Side Resources (April 29, 2014), http://www.iso-ne.com/static-assets/documents/committees/comm_wkgrps/prtcpnts_comm/pac/mtrls/2014/apr292014/a8_generic_capital_costs_of_supply_side_resources_rev2.pdf.

The actual capital costs of new resources may be different from these generic estimates because of the following factors:

- State of technology development

- Changes in material, labor, and overhead costs

- Supply-chain backlogs or oversupply

- Specific site requirements

- Regional cost differences

- Difficulties in obtaining site and technology approvals

In addition, experience suggests that many construction projects encounter unforeseen design and construction problems that tend to increase costs.

## Strategic Transmission Analyses—Generator Retirement Analysis

Another aspect of the Strategic Transmission Analyses has assessed transmission issues associated with potential generator retirements. The initial phase of the generator retirement study was completed in 2012, with additional sensitivity analyses continuing through 2013 and 2014.

The Strategic Transmission Analysis Generator Retirement Analysis examined the loss of approximately 8,300 MW of coal- and oil-fired generating units. The results showed these retirements would cause resource shortages and, to a lesser degree, transmission-reliability constraints in New England that would require over 6,000 MW of resources to be retained, repowered, or replaced to satisfy the region’s Installed Capacity Requirement (see Section 4.1.1). The repowering of many of these existing generators with natural gas would not require a major expansion of new system resources or improvements to the transmission system, although more natural gas transportation would be required. The addition of new capacity electrically located at the region’s energy trading hub (the Hub) (see Section 2.4), or the addition of new capacity deliverable to the Hub, would allow the region to serve most of its load reliably.

The Southeast Massachusetts and Connecticut load zones, however, may need some resources to address zonal or more local transmission reliability concerns that would vary depending on the timing and location of retirement requests. As noted in Section 4.1.3.3, of the potential generation retirements studied, both Brayton Point and Norwalk Harbor have submitted nonprice retirement requests.

## Analysis of Market-Resource Alternatives (MRAs) in Load Pockets

Regional System Plans provide considerable information on the desired amounts, types, locations, and performance requirements of resources for meeting system needs. In general, developing resources in load pockets is beneficial, especially the load pockets with exposure to potential generator retirements. However, assessing the suitability of resources during the planning process can be challenging because of the wide variability of the characteristics, locations, and possible combinations of resources, such as central station and distributed generation resources, end-use efficiency, and storage technologies.

In response to PAC requests for more details about resources that could meet system needs, the ISO applied the lessons learned from the Vermont/New Hampshire and Greater Hartford Central Connecticut studies to a study of the Southeast Massachusetts/Rhode Island area. The study demonstrated how resources of various sizes and at various locations could meet thermal system performance requirements for 2022.

The study identified the critical load levels and a hypothetical combination of generation, demand reduction, and transmission that could address thermal and voltage issues in the area. This combination of generation and load-reduction measures, located at the proper locations, were shown to help mitigate thermal needs, coupled with a minimal amount of transmission upgrades to mitigate voltage violations.

In total, approximately 940 MW of MRAs were needed. Specifically, approximately 900 MW of generation and 40 MW of demand reductions were needed as well as 43 MVAR of reactive support to resolve thermal and voltage system needs under system normal and N-1 conditions. This load pocket MRA study used the same N-1 assumptions as the SEMA/RI Needs Assessment and addressed the same violations identified in that study.

The ISO intends to continue analyzing MRAs in load pockets and will undertake additional MRA analysis in early 2015.

## Summary

The ISO is conducting a number of studies to quantify the risks identified through the Strategic Planning Initiative, many of which are interrelated, and inform stakeholders of other strategic planning issues facing the region. The region has implemented several measures and is developing others to improve the reliable and economic performance of the power system.

The operational challenges experienced during winter 2013/2014 highlighted the need for the ISO to manage energy production limitations of electric power generators. The region’s unsustainable and steadily increasing dependence on natural gas for power generation is evident. The diminished operating performance of infrequently operated oil and coal generators, the potential fuel-availability issues, and other physical challenges amplify this reliability risk.

Many improvements to system operations and the region’s wholesale electricity markets, actively under development, will address these issues. The region has developed short-term mitigation measures that bolstered 2013/2014 winter reliability. Modifications to the day-ahead and real-time markets, as well as efforts to procure additional reserves, will help reach medium-term solutions, while changes to the Forward Capacity Market will achieve the longer-term solutions. Recent and planned improvements to the regional and interregional natural gas infrastructure also have been analyzed to assess the likelihood of its expansion for meeting New England’s increasing demand for natural gas to produce electric power. Fuel certainty could be improved in a number of ways:

- Firm contracts with natural gas pipeline operators would allow existing infrastructure to be more fully utilized and would support the building of new natural gas pipeline capacity.

- Firm contract with suppliers, including LNG operators, would improve the likelihood of generators procuring natural gas.

- Increased flexibility of scheduling natural gas would allow generators to respond better to changing system conditions.

- Use of existing and new dual-fuel capability at generating plants would provide alternative supplies of fuel when natural gas supplies are limited.

- Adequate local storage of dual fuel, especially oil, would increase generation reliability.

- Increased efficient use of natural gas and electricity would allow greater use of available pipeline capacity by generators.

Existing and pending state, regional, and federal environmental regulations will require many generators to consider, between 2015 and 2022, adding air pollution control devices; modifying or reducing water use and wastewater discharges; and in some cases, limiting operations. Environmental controls necessary for compliance with these regulations will likely add capital investment at some generators, increase operating compliance costs at many generators, and involve additional operational restrictions at certain generators. Most of the at-risk capacity faces compliance or retirement decisions later this decade, which is expected to affect positions in upcoming Forward Capacity Auctions. The ISO continues to identify such generators and study potential impacts.

The ISO also continues to analyze wind-integration issues and has made progress implementing wind forecasting and dispatch. While the level of wind resources has not yet triggered additional requirements, the ISO is working toward increasing system flexibility and has increased its operating reserve to address resource performance issues. The ISO is improving the modeling of wind resources and is updating the process for pursuing elective upgrades.

The wind-integration component of the Strategic Transmission Analysis is developing conceptual additions to the transmission system that would enable onshore wind resources to reliably serve load. The 2011 Economic Study showed the effects of integrating varying amounts of wind on production cost, load-serving energy expense, and congestion, as well as the need for transmission development to enable wind resources to serve the region’s load centers. The ISO will continue to engage stakeholders on the issues challenging the wind-interconnection process and the performance of the system with wind resources in locally constrained areas.

While existing amounts of PV have yet to have a significant impact on system operations, the ISO is working on several initiatives aimed at facilitating its reliable and efficient integration. The regional goal is to have over 2,000 MW of distributed generation by 2023, of which 1,800 MW is expected to be PV. The ISO successfully completed the first multistate forecast of PV development and is working with stakeholders to accomplish the following:

- Develop a short-term solar forecast for use by system operators

- Develop a method to consider expected amounts of PV in long-term planning

- Address the potential reliability risks posed by growing penetrations of PV

The results of the 2012 Economic Study highlighted the most suitable locations for developing different resources without causing congestion; the effects of using efficient, low-emitting resources, increased amounts of renewable energy, and energy efficiency; and the least suitable locations for unit retirements. The ISO has presented the PAC with draft results for the 2013 Economic Study, which is evaluating the effect of increasing the acceptable loss-of-source limits in New England.

The Strategic Transmission Analysis, which is assessing transmission issues associated with potential generator retirements, shows that the loss of these resources would cause resource shortages and transmission-reliability constraints requiring the retention, repowering, or replacement of much of the resource capacity. The study further showed that, in the event of these retirements, adding new capacity in electrical proximity to the Hub could reliably serve most of the region’s load. The Strategic Transmission Analyses may provide insights to develop Strategic Planning Initiative solutions focusing on market design and transmission planning.

The ISO’s analysis of market resource alternatives in the SEMA/RI load pocket shows the critical load levels and hypothetical supply-side and load-reduction resources that could eliminate thermal overloads for normal and N-1 contingency conditions.

# Planning Coordination, Studies, and Initiatives

ISO planning activities are coordinated with neighboring systems, across the Eastern Interconnection, and nationally with federal and regional governmental representatives and the six New England states. State initiatives and policies have a significant impact on the wholesale electricity markets and transmission developed to meet system needs, specifically influencing the timing, type, and location of resources and transmission infrastructure.

## Interregional Coordination and Initiatives

The ISO is participating in numerous national and interregional planning activities with DOE, the Northeast Power Coordinating Council, and other planning authority areas in the United States and Canada. The aim of these projects, as described in this section, is to ensure the coordination of planning efforts for enhancing the widespread reliability of the interregional electric power system. The ISO also conducts studies with other entities within and outside the region, including neighboring areas. These projects, for example, improve production cost models, share simulation results, investigate the challenges to and possibilities for integrating renewable resources, and address other common issues affecting the planning of the overall system.

The ISO must identify and resolve interregional planning issues, as identified in needs assessments and solutions studies, consistent with the mandatory reliability requirements of the North American Electric Reliability Corporation. Interconnections with neighboring systems allow for the exchange of capacity and energy, and tie lines facilitate access to a diversity of resources and compliance with environmental obligations and the more economic, interregional operation of the system. Quantifying these benefits, identifying potential needs for additional interconnections, and coordinating the planning of the interconnected system are becoming increasingly important.

### Eastern Interconnection Planning Collaborative Studies of the Eastern Interconnection

The electric power planning authorities of the Eastern Interconnection, including ISO New England, formed the Eastern Interconnection Planning Collaborative (EIPC) to address their portion of North American planning issues and manage the process for combining the existing regional transmission expansion plans and analyzing the interconnection-wide system. EIPC received a grant from DOE to conduct studies of the Eastern Interconnection, and EIPC is continuing to coordinate base cases and conduct analyses without DOE funding.

EIPC is working with DOE to apply the remaining funds of the grant to support an analysis of the electric power system’s interface with the natural gas sector. The study has four main objectives:

- Develop a baseline assessment of the existing natural gas and electric power system infrastructures

- Evaluate the capability of the natural gas system to meet the needs of the electric power system

- Identify contingencies on the natural gas system that could adversely affect electric power system reliability and vice versa

- Review operational and planning issues, including fuel-assurance issues affecting the availability of dual-fuel-capable generation

EIPC must submit a report to DOE in June 2015 on the gas-electric study. The six participating planning authorities leading the study effort are ISO New England, New York, PJM, TVA, MISO (including the Entergy System), and Ontario (see Section 6.2.3.4).

EIPC’s work in 2013 also included analyzing “roll-up” cases, which combined each region’s electric power system plan into a comprehensive model of the Eastern Interconnection. A draft report of the roll-up cases was posted for comment in December 2013, and a final report addressing stakeholder comments was posted in February 2014. The results show that the future transmission system as currently planned is capable of transferring power over long distances throughout the Eastern Interconnection above the long-term firm commitments modeled in the roll-up cases. The EIPC has developed a new process for gathering stakeholder input based on the existing regional stakeholder processes, and the planning authorities are soliciting feedback from stakeholders on potential scenarios to be analyzed during 2014. The EIPC will revise the base case for 2023, which the individual regions will use to analyze transmission build-outs and unit retirements. At EISPC’s request and with input from stakeholders, the EIPC will also examine heat wave and drought conditions.

### Electric Reliability Organization Overview

As the RTO for New England, the ISO is responsible for ensuring that its operations and planning comply with applicable NERC standards. In addition, the ISO has participated in regional and interregional studies required for compliance.

Through its committee structure, NERC, which is the FERC-designated Electric Reliability Organization (ERO), regularly publishes reports that assess the reliability of the North American electric power system. Annual long-term reliability assessments evaluate the future adequacy of the power system in the United States and Canada for a 10-year period. The reports project electricity supply and demand, evaluate resource and transmission system adequacy, and discuss key issues and trends that could affect reliability. Summer and winter assessments evaluate the adequacy of electricity supplies in the United States and Canada for the upcoming summer and winter peak-demand periods. Special regional, interregional, or interconnection-wide assessments are conducted as needed.

In December 2013, NERC issued its annual Long-Term Reliability Assessment (LTRA), analyzing reliability conditions across the North American continent. This report describes transmission additions, generation projections, and reserve capability by reliability council area. Within a 10-year planning horizon, both ReliabilityFirst Corporation (RFC) and NPCC are expected to have sufficient reserves to meet reliability needs. Projected load growth continues to be sluggish in both areas due to slower economic growth, efficiency gains from new appliance standards, increased participation in demand-side management programs, and additional reliance on behind-the-meter generation. Challenges noted for NPCC include aging infrastructure issues, the integration of variable resources, growing dependence on natural gas generation, and the retirement of fossil-fueled and nuclear generation. Challenges noted for the RFC area include a large amount of fossil-fueled generation at risk of retirement during the assessment period due to environmental retrofit costs. While resource adequacy is not an overall concern, localized reliability concerns may need to be addressed.

### IRC Activities

Created in April 2003, the ISO/RTO Council (IRC) is an industry group consisting of the nine functioning ISOs and RTOs in North America. These ISOs and RTOs serve two-thirds of the electricity customers in the United States and more than 50% of Canada‘s population. The IRC works collaboratively to develop effective processes, tools, and standard methods for improving competitive electricity markets across much of North America. Each ISO/RTO manages efficient, robust markets that provide competitive and reliable electricity service, consistent with its individual market and reliability criteria.

While the IRC members have different authorities, they have many planning responsibilities in common because of their similar missions. As part of the ISO/RTO authorization to operate, each ISO/RTO independently and fairly administers an open, transparent planning process among its participants. These activities include exchanging information, treating participants comparably, resolving disputes, coordinating infrastructure improvements regionally and interregionally, conducting economic planning studies, and allocating costs. This ensures a level playing field for infrastructure development driven efficiently by competition and meeting all reliability requirements.

The IRC has coordinated a number of reports, and filings and presentations with national government agencies. The 2013 North American Wholesale Electricity Demand-Response Comparison summarizes wholesale electricity demand-response programs, products, and services administered by the ISOs and RTOs in North America. The IRC has worked with EPA, the states, and all interested parties on proposed CO2 regulations that respect electric power system reliability and are compatible with the efficient dispatch of the electric grid. Common issues have been identified for FERC filings, such as compliance with FERC Order No. 1000 (see Section 7.2.1). IRC members also have coordinated on a number of technical issues, such as the use of software and the sharing of planning techniques.

### Northeast Power Coordinating Council Studies and Activities

The Northeast Power Coordinating Council is one of eight regional entities located throughout the United States, Canada, and portions of Mexico responsible for enhancing and promoting the reliable and efficient operation of the interconnected bulk power system. NPCC has been delegated the authority by NERC to create regional standards to enhance the reliability of the international, interconnected bulk power system in northeastern North America. As a member of NPCC, the ISO fully participates in NPCC-coordinated interregional studies with its neighboring areas.

NPCC assesses seasonal reliability and, periodically, the reliability of the planned NPCC bulk power system. It also evaluates annual long-range resource adequacy. All studies are well coordinated across neighboring area boundaries and include the development of common databases that can serve as the basis for internal studies by the ISO. Assessments of ISO New England demonstrate full compliance with NERC and NPCC requirements for meeting resource adequacy and transmission planning criteria and standards.

### Northeastern ISO/RTO Planning Coordination Protocol

ISO New England, NYISO, and PJM follow a planning protocol to enhance the coordination of planning activities and address planning seams issues among the interregional balancing authority areas. Hydro-Québec TransÉnergie, the Independent Electric System Operator of Ontario, and the Transmission and System Operator Division of New Brunswick Power participate on a limited basis to share data and information. The key elements of the protocol are to establish procedures that accomplish the following tasks:

- Exchange data and information to ensure the proper coordination of databases and planning models for both individual and joint planning activities conducted by all parties

- Coordinate interconnection requests likely to have cross-border impacts

- Analyze firm transmission service requests likely to have cross-border impacts

- Develop the Northeast Coordinated System Plan

- Allocate the costs associated with projects having cross-border impacts consistent with each party’s tariff and applicable federal or provincial regulatory policy

To implement the protocol, the group formed the Joint ISO/RTO Planning Committee (JIPC) and the Inter-Area Planning Stakeholder Advisory Committee (IPSAC) open stakeholder group. Through the open stakeholder process, the JIPC has addressed several interregional, balancing-authority-area issues. The following list shows several key planning issues summarized in the 2013 Northeast Coordinated System Plan (NCSP13) that affect the broad region and additional studies that have been presented to the IPSAC:

- Coordination and sharing of transmission study databases, critical contingency lists, and short-circuit equivalents

- Identification of improved planning techniques, modeling, and software tools

- Coordination of interconnection queue studies and transmission improvements, such as upgrades for interconnecting the Cricket Valley Energy Center (Dover, NY) to the 345 kV line 398 (Pleasant Valley–Long Mountain)

- Coordinated production cost models and market-efficiency studies

- Evaluations of environmental regulations and their potential effects on the power systems

- Identification of issues and solutions facilitating the integration of intermittent resources

- Assessment of fuel diversity issues, including coordinated studies of the natural gas system

- Determination of the effect of demand-side resources on interregional planning

NCSP13 also serves as a baseline for interregional planning as the planning process continues evolving to comply with FERC Order No. 1000. JIPC activities also have coordinated compliance filings for this FERC order, particularly on interregional planning and cost-allocation issues.

### Interregional Transfers

Figure 7-1 shows the transfers that occurred with neighboring systems for 2013. The region imported approximately 14.5% of the net energy for load plus pumping load.

Figure 7-1: 2013 energy imports and exports by external area (GWh).

Notes: Imports are show as positive values, and exports are shown as negative values. Data are current as of the March 1, 2014, 90-day resettlement of 2013.

The ISO and the New York ISO are committed to creating a broader regional market and improving the efficiency of electricity trade between the regions. In 2010, the two ISOs commenced a joint project to evaluate the economic and operating performance of energy flows across their interconnected transmission network. The project’s two central objectives are to improve the economics of using the transmission ties between the regions and to leverage the regions’ capabilities to minimize congestion. This long-term project has two phases. Phase I, the Coordinated Transaction Scheduling project, seeks to improve the economic coordination between the two regions’ electricity markets. Phase II will focus on coordinated congestion management and network modeling.

## Federal Initiatives

The Energy Policy Act of 2005 (EPAct) requires the US Department of Energy and the Federal Energy Regulatory Commission to implement several reliability provisions. The requirements include ensuring the reliability of the transmission infrastructure and implementing enforceable reliability standards administered by the North American Electric Reliability Corporation.

### FERC Order No. 1000

FERC Order No. 1000, issued on July 21, 2011, sets forth additional requirements that build on Order No. 890, including regional and interregional planning procedures and cost allocation and the incorporation of “public policy considerations” into the planning process. The ISO filed compliance filings with FERC on October 25, 2012, and July 10, 2013. The October 2012 filing describes the means to identify and consider transmission needs driven by state or federal public policies. The July 2013 filing describes improvements to both the interregional planning process and interregional cost allocation.

On May 17, 2013, FERC issued a regional compliance order on the ISO’s and certain New England transmission owners’ proposed regional compliance with Order No. 1000. On June 17, 2013, the ISO submitted a request for rehearing of several aspects of the May 17, 2013 order addressing planning for public policy and rights of participating transmission owners. On November 15, 2013, the ISO filed additional tariff changes to implement its compliance with this order. The ISO has worked with stakeholders to comply with the order and is awaiting the final FERC orders.

### US Department of Energy Congestion Studies

DOE is required to conduct a study every three years on electricity transmission congestion and constraints within the Eastern and Western Interconnections. DOE posted the National Electric Transmission Congestion Study as a draft report for public comment in August 2014. Using the results of these studies and comments provided by the states and other stakeholders, the US Secretary of Energy may then designate any geographic area experiencing constraints or congestion on electricity transmission capacity as a National Interest Electric Transmission Corridor (National Corridor). A designation as a National Corridor merits federal concern and may enable FERC to exercise “backstop” authority to site transmission facilities. This would occur only under limited circumstances, such as when a state agency has failed to act on a siting application within a National Corridor for more than one year.

The draft Congestion Study showed the following key findings for the Northeast:

- Generation and transmission additions in the Northeast have contributed to lower overall congestion for 2009 through 2011 compared with previous years, particularly in New England.

- Congestion is also reduced because of lower demand, which is attributed to the economic recession of 2008–2009, energy efficiency, and demand-response programs.

- Some congestion still exists, however. Much of the congestion that remains in the Northeast reflects three factors:

- Transmission constraints continue to restrict the delivery of power into load centers in central New York and the New York City and Long Island areas.

- Increased levels of low‐cost wind generation in concentrated locations west of the major load centers of the Northeast exceed the capability of transmission facilities.

- The Northeast is addressing administrative and institutional issues arising from different market rules, scheduling practices, and transmission reservations that obstruct the more effective use of facilities between neighboring RTOs and ISOs.

The DOE intends to release a stand-alone transmission data document annually, rather than combining it with the triennial congestion studies. Transmission Constraints and Congestion in the Western and Eastern Interconnections, 2009-2012 compiles publicly available data on transmission constraints and congestion for 2009 through 2012. The report provides timely transmission data to the public to aid the development of public and private analyses on a range of electricity topics.

### Quadrennial Energy Review

Since January 2014, DOE has been developing the first part of its multi-year Quadrennial Energy Review (QER), a comprehensive analysis of energy and electricity production and delivery systems in the United States. The US Secretary of Energy, Ernest Moniz, described the QER as a roadmap to modernize the country’s energy infrastructure in ways that will support the nation’s economic competitiveness and energy security, as well as enable the country to move toward a low-carbon future. In the first year of this analysis, which will conclude in January 2015, DOE has focused on the nation’s energy infrastructure for transporting, transmitting, storing, and delivering energy.

DOE continues to conduct extensive stakeholder outreach to better understand unique regional challenges, including the retirement of aging generators in New England and its increased reliance on an already-constrained natural gas system (see Section 6.2). This outreach included stakeholder meetings in Providence, RI, and Hartford, CT, on April 21, 2013. The QER will not only address short-term energy infrastructure but the overall impacts of broader changes in climate and the challenges of both physical security and cybersecurity.

### Executive Orders on Cybersecurity

Concurrent with the development of the QER, the Obama administration continues to direct federal resources toward improving the security of the electric power grid. In February 2014, the National Institute of Standards and Technology released the Framework for Improving Critical Infrastructure Cybersecurity, the culmination of a year-long effort to provide owners and operators of critical digital infrastructure with guidelines to better secure their assets. The development of the framework was directed by a February 2013 executive order and included participation from members of the ISO/RTO Council.

### FERC Directive on Physical Security

In March 2014, FERC directed the North American Reliability Corporation to initiate a process to develop a new standard to improve the physical security of critical components of the electric grid. FERC gave NERC several months to work with industry to craft a standard that identifies critical assets and develops a strategy for protecting these facilities.

## Regional Initiatives

State, regional, and federal initiatives and policies have a significant impact on the wholesale electricity markets and transmission developed to meet system needs, specifically influencing the timing, type, and location of resources and transmission infrastructure. While not an all-inclusive list, this section discusses several policies, laws, and activities affecting the regional power system.

### Coordination among the New England States

The New England states have worked together continually to identify, discuss, and address energy issues of common interest. Even with this history of cooperation, each state has a unique set of energy policy objectives and goals.

Each of the New England states is actively involved in the ISO’s regional planning process, individually and through the New England States Committee on Electricity (NESCOE). NESCOE serves as a forum for representatives from the states to participate in the ISO's decision-making processes, including those dealing with resource adequacy and system planning and expansion.

NESCOE has been active in the study of natural gas supply and electric power generation. In 2012 and 2013, NESCOE completed a three-phase study to evaluate the sufficiency of gas infrastructure to support electric power generation in New England from 2014 to 2029. The most recent study recommended the construction of a cross-regional natural gas pipeline to alleviate long-term supply constraints under the study’s base case and high-demand scenarios. In January 2014, NESCOE also requested assistance from the ISO in support of the governors’ agreement on improving electric transmission infrastructure for clean energy and increasing natural gas capacity (refer to Section 6.2.4.4). The ISO is committed to working with the states and NEPOOL participants on any proposed changes to its responsibilities under the OATT.

In addition to NESCOE, the ISO works collaboratively with the New England Conference of Public Utilities Commissioners (NECPUC), the New England governors’ offices, and the states’ consumer advocates. The ISO provides monthly updates to the states on regional stakeholder discussions regarding the regional planning process and the wholesale electricity markets.

The New England states are active participants in the interconnection-wide planning for the Eastern Interconnection. The Eastern Interconnection States Planning Council (EISPC) is an organization of 39 states and eight Canadian provinces in the Eastern Interconnection electric transmission grid, including representatives from New England, responsible for participating with the planning authorities that are part of the EIPC (see Section 7.1.1). Funded by a DOE Funding Opportunity Announcement, the EISPC comprises public utilities commissions, governors' offices, energy offices, and other key government representatives and provides input to the EIPC study effort. As a planning authority, the ISO has provided technical support to the EISPC. The ISO, NESCOE, and NEPOOL work closely to coordinate New England’s participation in all EISPC and EIPC activities.

### Consumer Liaison Group

The ISO and regional electricity market stakeholders created the Consumer Liaison Group (CLG) in 2009 to facilitate the consideration of consumer interests in determining the needs and solutions for the region’s power system. With representatives from state offices of consumer advocates and attorneys general, large industrial and commercial consumers, chambers of commerce, and others, the CLG meets quarterly to address various consumer issues. With the input of CLG members, a Coordinating Committee guides CLG meeting agendas and ideas for special guest speakers and discussion topics.

In 2013, the CLG’s discussions focused on New England’s dependence on natural gas for power generation, the region’s constrained natural gas pipeline system, and associated impacts on consumers. On May 28, 2014, the CLG Coordinating Committee and the ISO issued the 2013 Report of the Consumer Liaison Group, which summarizes the activities of the CLG in 2013.

## ISO Initiatives

In addition to the Strategic Planning issues discussed in Section 6, the ISO is involved in a number of other initiatives aimed at improving the wholesale electricity markets, developing and integrating new technologies, and enhancing operating and planning procedures to enhance system reliability.

### Improving the Wholesale Electricity Markets

The ISO annually assesses the wholesale electricity markets to better understand problems to be addressed and to determine whether the market design or other measures warrant any changes. The ISO uses this information and the results of RSP studies to develop market design changes through an open stakeholder process. Several market design projects address some of the challenges identified in the Strategic Planning Initiative (as discussed in Section 6). For example, some projects will improve the coordination between the electric power and natural gas sectors and others (i.e., modifications to the FCM) will provide incentives that improve resource performance. One of these projects will allow demand response to set market-clearing prices that more closely reflect the costs of activating these resources in the Day-Ahead Energy Market and Real-Time Energy Market.

### Updates on Developing and Integrating Smart Grid and Other New Technologies

The ISO strives to keep up to date with new technologies that can have an impact on the region’s electric power grid. As policymakers set targets and allocate public funds for developing smart grid initiatives and renewable resource generation, the ISO analyzes the effects of these technologies on system operations and reliability. Several of the technology developments and challenges affecting the planning of the New England region involve integrating smart grid equipment, improving operator awareness and system modeling through the use of phasor measurement units (PMUs), and using high-voltage direct-current (HVDC) facilities and flexible alternating-current transmission system (FACTS) devices.

#### Participation in Developing Industry Standards and Other Professional Activities

Several municipal electric utilities and distribution system owners have installed advanced metering infrastructure (AMI) and technology. These technologies facilitate the installation of distributed resources and price-responsive demand. The ISO currently participates in several research projects sponsored by DOE, the Power System Engineering Research Center (PSERC), and the Electric Power Research Institute (EPRI) that support the successful integration of advanced technologies.

EIA notes that many commercial and industrial customers appear to have lower penetration rates for advanced metering infrastructure because they likely already have installed more sophisticated analog meters enabling participation in time-of-use or interruptible tariffs. EIA reports that the 2012 AMI penetration rate in New England was 7.6% of all reported meters. Maine has the highest penetration rate at 99.1%, while the rest of the New England states have penetration rates of 0 to 27%.

The ISO also is actively participating in the development of the national smart grid interoperability standards, led by the National Institute of Standards and Technology, to establish protocols that provide common interfaces for smart grid equipment. Additionally, as a part of an ISO/RTO Council project with other ISOs/RTOs, the ISO is providing technical and other support for the development of demand-response-related standards by NIST and the North American Energy Standards Board (NAESB). ISO staff and stakeholders remain professionally active in the Institute of Electrical and Electronics Engineers (IEEE), a society that serves to educate its members and the public at large, as well as develop standards for the interconnection and operation of smart grid technologies.

#### PMU Infrastructure and Data Utilization

In New England, PMUs are installed at 40 substations, one phasor data concentrator (PDC) is at the ISO, and seven PDCs are at participating transmission owners. Additionally, the region has communication infrastructure to support streaming PMU data from substations to transmission owners and then to the ISO.

PMUs have improved overall system security through wide-area monitoring and situational awareness. The ISO has also improved the modeling of generators and the system through the analysis of PMU data that helps identify modeling parameters and reconstruct system events. The ISO currently uses PMU data for an application called the Region of Stability Existence (ROSE), which computes operational voltage stability boundaries and margins and compares these limits with actual operating conditions. Longer-term, the ISO is exploring the use of PMU data to enhance the quality of the state estimator, which provides near real-time quantities of parameters necessary to operate the system.

#### HVDC and FACTS

The application of power electronics to the power system through high-voltage direct-current and flexible alternating-current transmission system technologies can enhance the performance of the transmission system. HVDC and FACTS use a combination of solid-state switches and computerized automation that enables nearly instantaneous customized control of real or reactive power flows—far faster than traditional electromechanical switches. HVDC has been applied to the New England system interconnections with Québec and to New York under the Long Island Sound. As mentioned in Section 6.6.3.2, a part of the Strategic Transmission Analysis for wind is the study of thyristor-controlled series-compensation FACTS devices. FACTS applications have provided a much-needed boost to the transmission system and offer some other technical advantages, especially when dynamic voltage support is needed. Figure 7-2 shows the existing and planned FACTS devices in New England.

Figure 7-2: Existing and planned FACTS devices in New England.

Note: The acronyms and abbreviations in the key refer to the following terms: HVDC = high voltage, direct current. VSC = voltage source converter. SVC = static voltage ampere reactive (V) compensator. STATCOM = static synchronous compensator. DVAR = dynamic voltage ampere reactive.

Both HVDC and FACTS are regularly considered as part of transmission planning studies when their applications economically meet system or generator interconnection needs. For example, the HVDC controls for Highgate were replaced in November 2012. Changes to the Chester static VAR compensator (SVC) control settings were completed in 2010, and dynamic voltage ampere reactive systems (DVARs) have been applied to stabilize wind farms, such as Kibby and Kingston (see Section 5.4.1). As shown in Figure 7-3, future merchant and elective HVDC projects are under consideration as part of additional interconnections with Québec, New Brunswick, and New York, and as part of the interconnections within New England between areas with a large potential for wind power development (see Section 6.6) and regional load centers.

|  | Representative Projects and Concept Proposals. A; Northern Pass—Hydro-Québec/ Northeast Utilities. B; Northeast Energy Link— Emera Maine/National Grid. C; Green Line—New England ITC. D; Bay State Offshore Wind Transmission System— Anbaric Transmission. E; Northeast Energy Corridor—Maine/New Brunswick/Irving. F; Muskrat Falls/Lower Churchill—Nalcor Energy. G; Maine Yankee—Greater Boston. H; Maine—Greater Boston. I; Northern Maine—New England. J; Plattsburgh, NY—New Haven, VT. K; New England Clean Power Link— TDI New. |
| --- | --- |

Figure 7-3: Large-scale transmission in New England, including some proposed direct-current transmission.

### Draft Transmission Planning Process Guide and Draft Transmission Planning Technical Guide

The ISO developed guides that document both the implementation of the regional planning process described in Attachment K of the OATT and the associated technical assumptions. Both documents reflect stakeholder input. The Transmission Planning Process Guide (Process Guide), finalized at the end of 2013, discusses the development of needs assessments and solution studies (see Section 5.4), including the opportunities for stakeholder involvement. The Transmission Planning Technical Guide (Technical Guide), still in draft form, describes the current standards, criteria, and assumptions used in transmission planning studies of the regional power system.

The Process Guide will need to be updated to reflect changes in the planning process required by FERC Order No. 1000. In an update of the Technical Guide, the ISO is reflecting stakeholder comments on current practices and is examining updates to the planning process and assumptions, reflective of these comments. The ISO also is examining the use of probabilities to better represent system conditions by reflecting the correlation of load levels, generator outages, the dispatch of intermittent resources, and other factors. This analysis may inform assumptions used in planning studies and assist with identifying new simulation tools. The ISO is beginning the stakeholder process to discuss this information, an effort that will likely extend beyond 2015.

## State Initiatives, Activities, and Policies

The New England states have worked together continually to identify, discuss, and address energy issues of common interest. Over the past few years, the New England states have implemented numerous and varied energy policies and initiatives that have consistently focused on advancing energy efficiency, mitigating costs through long-term contracting, increasing the development of renewable resources, and reducing pollutants from certain generating facilities.

Even with this history of cooperation, each state has a unique set of energy policy objectives and goals. This section presents recently implemented laws, policies, and initiatives that affect regional system planning. While not an all-inclusive list of state initiatives, activities, and policies, this section discusses several policies recently considered and laws enacted in the six New England states.

### Connecticut

With greater demands on natural gas, the Connecticut Department of Energy and Environmental Protection (DEEP) has stated that it will work with gas pipeline developers and local distribution companies to ensure that natural gas transmission capacity increases to meet the anticipated growth in demand. DEEP has also stated that it will work with stakeholders, including the ISO, to further coordinate efforts between the electric power and gas industries for addressing the region’s increased dependence on natural gas and the effects on the reliability of the electric power system.

In June 2013, Senate Bill 1138 was enacted, restructuring the state’s Renewable Portfolio Standard (RPS). The legislation accomplishes the following:

- Allows large-scale hydro to count toward the RPS target but only in the event of a verified shortfall in Class I supply (up to 1% of electric energy provided in 2016 and no more than 5% by 2020)

- Gives DEEP the authority to solicit proposals and direct electricity distribution companies to enter into long-term power-purchase agreements with various renewable energy sources

- Expands support for small hydropower by increasing Class I hydro eligibility from 5 MW to 30 MW

- Calls for a gradual reduction in the value of renewable energy certificates (RECs) received by biomass and landfill gas projects

On July 8, 2013, DEEP issued a request for proposals to solicit bids from developers of Class I renewable energy projects to serve up to 4% of Connecticut’s load. This RFP is the first of many solicitations authorized by the RPS restructuring bill. Through long-term contracting, Connecticut hopes to procure enough renewable energy to meet its steadily increasing Class I RPS requirement and avoid alternative compliance payments (ACPs) set at $55/MWh by statute. In 2014, Connecticut utilities and suppliers must obtain 11% of their energy supply from Class I renewable energy sources, increasing to 20% by 2020.

On April 22, 2014, the state legislature’s Regulation Review Committee approved wind-siting regulations developed by the Connecticut Siting Council, lifting a three-year moratorium on new wind projects sited in Connecticut. The regulations establish a new framework for evaluating wind proposals in the state, with consideration given to abutting properties, visual impacts, noise impacts, ice-throw potential, blade shear, shadow flicker, setback distances, and decommissioning plans. The regulations became effective on May 1, 2014.

As part of Connecticut’s 2013 Comprehensive Energy Strategy, the state has committed to investing in advanced metering and other technologies to further Connecticut’s demand-response programs. The vast majority of Connecticut’s electricity customers still have traditional meters, which only measure gross monthly usage and provide no information to consumers on their time of use, demand, or other usage characteristics. Connecticut sees the potential to further reduce peak energy demand through greater adoption of demand response and investment in technologies like advanced metering.

The Connecticut General Assembly passed no major energy legislation in 2014.

### Maine

In January 2014, the Maine Public Utilities Commission (MPUC) issued a report on geomagnetic disturbance (GMD) and electromagnetic pulse (EMP) protections for the electric power grid. This report noted that GMD and EMP risks present a serious threat to the reliability of the power system and recommends that stakeholders examine the costs and benefits associated with possible GMD and EMP mitigation. The risk analysis study group is meeting through 2014 and plans to identify a Maine-specific path forward for identifying actual costs of mitigation and determining where such investment should be made.

In March 2014, MPUC, the Governor’s Energy Office, and the Office of Public Advocate released a study describing the need for additional natural gas pipeline capacity into New England to lower electricity prices. The study, A Review of Natural Gas Capacity Options, was commissioned pursuant to the Omnibus Energy Act passed in 2013, which directed MPUC to evaluate the costs and benefits of additional natural gas pipeline capacity into New England. The report describes the impact of pipeline capacity on electricity prices and concludes that incremental natural gas pipeline capacity into the region would lower regional natural gas prices and benefit both Maine and New England customers.

MPUC has opened a proceeding to investigate how to improve the reliability of electricity service in the northern portion of the state not administered by the ISO. Potential solutions being considered include adding local generation and demand response in northern Maine, adding transmission reinforcements with New Brunswick, and connecting Maine Public Service to the rest of New England.

The Maine Solar Energy Act was created in 2014. The law notes that encouraging the development of solar energy in Maine is in the public interest and requires MPUC to develop a methodology and determine the value of distributed solar energy generation in the state. MPUC will summarize solar implementation options as part of a report and submit the report to the legislature by February 15, 2015.

### Massachusetts

In early January 2014, the Executive Office of Energy and Environmental Affairs released the first Massachusetts Global Warming Solutions Act (GWSA) Five-Year Progress Report. This report highlights the significant progress made and includes recommendations to more fully realize the potential of the GWSA. The progress report recommends the continued investment in information systems to support and manage the effective implementation of the GWSA. The report also recommends actions for the next five years:

- Focus on vehicle miles traveled, fuels, and land use

- Accelerate the implementation of “GreenDOT”

- Continue the aggressive implementation of energy efficiency

- Expand access to new clean energy resources and imports

- Continue to pursue offshore wind energy

- Aggressively pursue “supplemental” strategies

In June 2014, the Massachusetts’ Department of Public Utilities (DPU) issued an order that outlined the anticipated policy framework for time-varying rates. In this order, the department concluded that the basic service provided by utilities should include time-varying rates for all classes of customers upon the deployment of advanced metering technology, which should reduce costs for everyone, including those who do not respond to price signals. The order suggested that implementing time-of-use rates, with the deployment of advanced metering, marketing, outreach, and education, would require additional time.

In a corresponding proceeding, the DPU released an order that requires each electric power distribution company to submit a 10-year grid-modernization plan outlining how it will achieve four grid modernization goals, including (1) reducing the effects of outages; (2) optimizing demand, which includes reducing system and customer costs; (3) integrating distributed resources; and (4) improving workforce and asset management.

In 2010, Governor Patrick established a goal of having 250 MW of PV installed in the state by 2017. In 2013, the governor announced that the state had reached the goal three years early and subsequently increased the goal to 1,600 MW of PV installed by 2020.

In 2014, the Massachusetts’ legislature passed a bill, H 4385, An Act Relative to Credit for Thermal Energy Generated with Renewable Fuels, which increases the net-metering cap on public projects from 3% to 5%, and similarly raises the 1% cap for private projects to 4%. This legislation also creates a 17-person task force to study the long-term viability of net metering. The task force is charged with developing recommendations on incentives and programs to support the deployment of the state’s goal of 1,600 MW of solar generation in the state. The task force must submit a report to the legislature before April 1, 2015, on the costs and benefits of the existing net-metering framework that must include recommendations for legislative or regulatory reforms to encourage the continued expansion of solar generation in the state.

### New Hampshire

In early 2013, the New Hampshire Public Utilities Commission (PUC) opened an investigation to evaluate, among other things, the generation owned by Public Service of New Hampshire (PSNH) and the long-term viability of the current “hybrid” model for providing default service to PSNH customers. In June 2013, PUC staff concluded in a report that the status quo is not viable. Similarly, in November 2013, the Electric Utility Restructuring Legislative Oversight Committee requested the PUC to determine whether the sale of PSNH’s generation would be in the best overall economic interest of PSNH ratepayers and to submit a preliminary report by April 1, 2014.

The Preliminary Status Report Addressing the Economic Interest of PSNH’s Retail Customers as it Relates to the Potential Divestiture of PSNH’s Generating Plants states that, in the long-term, PSNH’s energy service rate will likely exceed prevailing market rates. The report also states that divesting PSNH assets would be more advantageous for PSNH default service customers, if the stranded costs were recovered from all customers. The report recommended that the PUC determine how to allocate the costs of the Merrimack Station scrubber and that the legislature should make changes to allow the PUC to fully review a divestiture. The legislature passed such a bill in June 2014, which if enacted, will grant the PUC the authority to make a determination and potentially order PSNH to divest.

In July 2013, New Hampshire enacted Senate Bill 191 directing the Office of Energy and Planning (OEP) and a new Energy Advisory Council (EAC) to review the state’s energy policies and develop a comprehensive 10-year energy strategy. An initial draft of the strategy, released on May 1, 2014, focused on augmenting the state’s energy-efficiency programs, renewable power generation, and use of smart grid technology. A final report to the governor and the legislature is due by September 1, 2014. Senate Bill 191 requires the strategy to consider the following topics:

- Projected demand for electricity and natural gas

- Existing and proposed electricity and natural gas generation and transmission facilities

- Renewable energy and fuel diversity

- Small-scale and distributed energy resources and energy storage technologies

- Energy efficiency and demand-side resources

The legislation acknowledges that the state’s energy strategy is part of a regional planning framework. Specifically, OEP and the EAC are charged with evaluating New Hampshire’s role in the regional electricity markets, the effects of the regional markets on the state’s energy policy goals, and how the state can most effectively participate at the regional level. The strategy requires the review and consideration of relevant ISO studies and plans.

Adjustments to the state’s Site Evaluation Committee (SEC) are proceeding along several fronts. In December 2013, the OEP completed an expansive study of the SEC pursuant to legislation passed earlier that year. The study evaluated the state’s energy facility siting process and, specifically, opportunities for public input to the siting process. The results of this study will be used to develop new administrative rules for the SEC’s siting criteria, which are due on January 1, 2015. In 2014, the state also passed legislation to change the composition of the committee, increase public participation in the application process, and create more specific criteria for wind projects.

House Bill 1129, passed in June 2014, requires the OEP to conduct a stakeholder process to develop a state energy-efficiency implementation plan. The legislation instructs the OEP to examine recommended energy-efficiency goals, various methods of expanding energy efficiency in NH, , the ratification of energy codes for new and existing buildings, funding mechanisms to provide incentives for energy efficiency, and other measures. The OEP must submit an initial report by November 1, 2014, and a final report by July 1, 2015.

### Rhode Island

Rhode Island’s Office of Energy Resources (OER) has initiated a process of updating the State Energy Plan. The updated plan will address energy security, energy efficiency, renewable energy procurement, and other opportunities to help “lay the foundation for an energy system that is secure and reliable, as well as clean, cost effective, and sustainable.” OER is in the process of finalizing the preliminary draft plan, which must undergo a technical and public review through the state’s planning program process before it is final. A final plan is expected by late 2014.

Rhode Island's Renewable Energy Standard (RES), established in June 2004, requires the state's retail electricity providers to supply 16% of their retail electricity sales from renewable energy resources by the end of 2019. Only 2% of the RES can be met with existing resources (in service before December 31, 1997). On February 10, 2014, the Rhode Island Public Utilities Commission issued an order delaying the 1.5% increase in the state’s RES scheduled for 2015 upon a finding of potential inadequacy of renewable energy supplies during that period. With a one-year delay of the 1.5% increase in 2015, the state’s RES will reach 14.5% by the end of 2019 instead of 16%.

During the 2014 legislative session, the Rhode Island General Assembly passed legislation entitled the Renewable Energy Growth Program, which expands the state’s commitment to distributed renewable energy generation. The state’s current DG program, which expires in 2014, has a goal of installing 40 MW of distributed generation by the end of 2014. The 2014 legislation creates a new five-year program with the goal of installing an additional 160 MW of distributed generation by the end of 2019. The new program will use electric distribution company tariffs to provide a multiyear stream of performance-based incentives to eligible renewable distributed generation projects.

The General Assembly also passed legislation establishing a framework for Rhode Island, in coordination with the other New England states, to make strategic investments in energy infrastructure and clean energy resources consistent with the New England governors’ regional energy infrastructure initiative. The Affordable Clean Energy Security Act gives Rhode Island the authority to participate in the development and issuance of regional or multistate competitive solicitations for the development and construction of regional natural gas pipeline infrastructure and regional electric transmission projects designed to bring renewable energy and large-scale hydropower to New England load centers. Natural gas and electric power distribution companies must file regional energy procurement proposals with the Rhode Island PUC for review and approval.

Additionally, the RI General Assembly passed the Resilient Rhode Island Act. This act replaces the existing Rhode Island Climate Change Commission with a new body, called the Executive Climate Change Council, charged with several duties, including increasing the deployment of the in-state generation of renewable energy and energy efficiency. The act requires the council to submit a plan to the governor and general assembly, no later than December 31, 2016, which must include strategies, programs, and actions to meet targets for reducing greenhouse gas emissions as follows:

- 10% below 1990 levels by 2020

- 45% below 1990 levels by 2035

- 80% below 1990 levels by 2050

### Vermont

While Vermont does not have a Renewable Portfolio Standard, it has adopted new policies aimed at increasing the amount of renewable resources in the state. In 2012, the initial 50 MW program cap, adopted in 2009, was increased to 127.5 MW over the 10-year term of the program. In 2013, the Vermont Public Service Board issued an order finding that additional renewable resources above the annual megawatt cap are eligible for standard-offer payments if they provide sufficient benefits to the operation and management of the electric power grid. This is specifically intended to mitigate transmission and distribution constraints. To date, no projects to meet such constraints have been identified.

In 2014, Vermont enacted legislation that increased the amount of resources eligible for the state’s net-metering program. Originally capped at 4% of a distribution utilities’ load, the quantity of renewable resources eligible for net metering increased to 15%.

### Summary of Renewable Portfolio Standards

The New England states have targets for the proportion of electric energy that load-serving entities must provide using renewable resources and energy efficiency. Options for meeting, or exceeding, the region’s RPS targets include developing the renewable resources in the ISO queue, importing qualifying renewable resource energy from adjacent balancing authority areas, building new renewable resources in New England not yet in the queue, developing “behind-the-meter” projects, and using eligible renewable fuels in existing generators. In addition, load-serving entities can make state-established alternative compliance payments if their qualified renewable resources fall short of providing sufficient Renewable Energy Certificates to meet the RPSs. ACPs also can serve as a price cap on the cost of RECs.

## Summary of Initiatives

The ISO’s planning activities are closely coordinated among the six New England states, with neighboring systems, across the Eastern Interconnection, and nationally. The ISO has achieved full compliance with all required planning standards and has successfully implemented the Northeastern ISO/RTO Planning Protocol, which has further improved interregional planning among neighboring areas and will continue to do so as part of regional compliance with Order No. 1000. Each New England state has a unique set of energy policy objectives and goals and continues to implement laws, policies, and initiatives that affect the regional system planning in New England.

# Key Findings and Conclusions

In accordance with all requirements in the Open Access Transmission Tariff, ISO New England’s 2014 Regional System Plan discusses the electrical system needs and the amounts, locations, and types of resource development that can meet these needs from 2014 through 2023. RSP14 also discusses the status of transmission system assessments, transmission system planning studies, and projects needed for meeting reliability requirements and improving the economic performance of the system. Other discussions include strategic planning challenges expected over the same 10-year planning horizon and how the region is analyzing and addressing these challenges. This section summarizes the key findings
of RSP14 and conclusions about the outlook for New England’s electric power system over the next 10 years.

## Forecasts of Peak Load, Energy Use, and Energy Efficiency

RSP14’s 10-year forecast for the annual use of electric energy is a 1.0% increase per year for 2014 through 2023. The forecast for the average growth in the summer peak demand is 1.3%. The forecast is materially the same as the RSP13 forecast. The 50/50 summer peak forecast for 2014 is 125 MW lower than the RSP13 forecast and 205 MW lower for 2022.

The ISO’s 2014 energy-efficiency forecast for 2018 to 2023, which also is similar to the EE forecast reported in RSP13, shows a regional annual average energy savings of 1,518 GWh, an average annual reduction in the peak demand by 205 MW, and a total reduction in the peak demand by 1,233 MW from 2018 to 2023. The summer regional load forecast net of EE resources is projected to increase at approximately half the projected growth rate of the 90/10 forecast without EE. The projections for net electric energy consumption and winter peak load show essentially no growth.

## Distributed Generation Forecast

The nameplate amount of photovoltaic resources approximately doubled from 250 MWAC in 2012 to about 500 MWAC in 2013 across the New England region. Projections of PV installations reach 1,800 MWAC by 2023, a forecast the ISO developed with stakeholder input.

The expansion of PV and other forms of distributed generation presents several complex technical issues that must be addressed to successfully operate and plan the system. These issues include the need for improving DG interconnection standards, developing a PV energy forecast, possibly extending the PV forecast to other forms of DG, improving the operating and forecasting tools, and using the DG forecast in planning studies. The ISO looks forward to working with stakeholders to resolve these issues.

## Systemwide and Local Area Needs for Capacity

RSP14 shows projections of the systemwide need for capacity, the amounts of retirements the system can withstand, and the locations where fast-start operating reserves would be beneficial. Natural-gas-fired generation and renewable resources currently in the generator interconnection queue, which shows 6,915 MW of active resource projects, may replace some of this retired capacity. Capacity zones are no longer defined using predefined boundaries but by objective criteria and studies. The new zones will be updated for each Forward Capacity Auction to reflect changing system conditions. RSP14 shows that the most favorable locations for new resource development are near load centers, particularly NEMA/Boston and SEMA/RI.

As recently as fall 2013, a surplus of capacity resources (both new and existing) was considered likely for FCA #8, but retirements were subsequently announced. Additional resources will be procured for the 2017/2018 capacity commitment period if deemed necessary in upcoming annual reconfiguration auctions. The region is projected to require 424 MW in 2019/2020, which would increase to a shortage of 1,155 MW in 2023/2024, accounting for the load and energy-efficiency forecasts and known retirements and assuming all resources with capacity supply obligations for FCA #8 remain in service.

Several older, fossil fuel generating facilities and a nuclear unit have announced retirements, and the high probability of additional resource retirements will likely accelerate the need for new capacity in the region. Additionally, generation owners could choose not to invest in environmental remediation measures called for in pending or required regulations, which could force these units to shut down. Market incentives are being designed and implemented to encourage the improved performance of existing resources and to develop needed new resources. The capacity needs of the system will likely be met by generators in the interconnection queue, imports from neighboring regions, and demand resources.

## Operating Reserves and Ancillary Services

Resources participating in the locational Forward Reserve Market are helping satisfy the operating-reserve requirements of the region overall and in major load pockets to address contingencies. The results of the operating-reserve analyses for 2014 through 2018 show that the representative operating-reserve requirements for Greater Southwest Connecticut are as much as 350 MW. Over the same period, the need for operating reserves in Greater Connecticut is as much as 1,100 MW during the summer, and similarly, the need for the BOSTON area is as much as 350 MW. The placement of fast-start, energy efficiency, and economical baseload resources in these load pockets will improve system performance. Transmission projects that increase the transfer capability into these areas or in other ways improve the electrical access of these areas to economical resources also enhance the economical and reliable performance of the system.

The need for flexible resources to provide operating reserves as well as other ancillary services, such as regulation and ramping, will likely increase as a result of unit retirements and the addition of intermittent resources, particularly wind and PV. To date, increasing the 10-minute operating-reserve requirement and adding seasonal replacement reserves have improved the systemwide performance for meeting peak load, ramping during changing system conditions, and the resource response to contingencies.

## Transmission Projects

Transmission projects are being completed to provide reliable electric power service throughout the system and to meet the demand in areas with significant load growth. From 2002 through June 2014, 559 projects have been put into service, totaling approximately $6.6 billion of new infrastructure investment. The descriptions of transmission projects in RSP14 are based on the June 2014 RSP Project List update, which includes 222 projects at a total cost of approximately $4.5 billion.

Most components of the Maine Power Reliability Program are either completed or under construction. The region also has made progress on the NEEWS project, which consists of several projects to serve load and improve transfer capability across southern New England. Two components—the Springfield and Rhode Island components—were placed in service during 2013. The Interstate component of NEEWS has received siting approval and is under construction. The Long-Term Lower SEMA project went into service in 2014. The needs assessment for the Central Connecticut Reliability Project and the Greater Hartford/Central Connecticut area was completed. A number of 115 kV upgrades that address local concerns and the ability to import power into western Connecticut as part of the broader Greater Hartford/Central Connecticut project have replaced the CCRP project. Two final alternatives for the Greater Boston area are being evaluated, and system components common to both alternatives have been identified.

Other transmission projects are being developed to meet reliability requirements where the development of resources is insufficient. In addition to the reliability benefits, transmission upgrades are supporting market efficiency, reflected by the low amounts of congestion and other out-of-merit charges, such as second-contingency and voltage-control payments. Additionally, elective and merchant transmission facilities are in various stages of analysis and development in the region and have the potential to provide access to renewable resources in remote areas of New England and neighboring regions, including Atlantic Canada and Québec.

## Market Resource Alternatives to Transmission

Transmission planning studies show the system needs and transmission additions required for the ISO’s continued compliance with NERC and NPCC reliability standards and criteria. Regional policymakers and developers of supply and demand resources and merchant transmission can use the detailed information in transmission planning studies to determine resource alternatives to transmission. For example, the transmission system needs assessments identify the critical load level that can be used to determine the amount of resources that would relieve transmission system constraints. Other types of transmission analyses and economic studies have been conducted to help inform stakeholders and government officials as they establish policies that affect the future planning and development of the system.

Interconnecting resources to load pockets and adding new capacity in electrical proximity to the Hub minimize the need for new transmission facilities. Although some local transmission improvements may be required, these locations are favorable even when considering the resources needed to compensate for the retirement of older oil- and coal-fired generating units. The ISO Strategic Transmission Analysis also conceptualized additions to the regional transmission system that would enable onshore wind resources to serve load reliably.

Economic studies have quantified system performance for varying amounts, locations, and types of resource expansion and retirements. The 2011 and 2012 Economic Studies showed the effects of integrating varying amounts of wind on the production costs, load-serving entity expenses, and emissions, as well as the need for transmission development to enable wind resources to serve the region’s load centers. The 2012 Economic Study highlighted the least suitable locations for unit retirements and the most suitable locations for developing different resources without causing congestion. The study showed the effects of using various amounts of energy efficiency and low-emitting resources, including renewable energy. More economic system performance is evident when resources with relatively low production costs are located at or delivered to load centers.

The 2013 Economic Study examines the effects of increasing imports on the Phase II interconnection with Québec, assuming that transmission limitations in both New York and PJM are relieved. The results show that the price of the imports affects the amount and times of increased transfers to New England. The study also shows that any economic savings resulting from reduced costs for regional energy production must be weighed against the increased costs of carrying higher operating reserves.

The ISO also conducted an analysis of market resource alternatives in the SEMA/RI area load pocket. The results quantified the minimum amounts and locations of both generation and demand resources that could satisfy N-1 system contingencies.

## Fuel Flexibility and Certainty

New England is an energy-constrained system that requires greater fuel certainty. The region’s heavy dependence on natural-gas-fired generation to meet its electricity needs has resulted in recent operating problems similar to those experienced during past extreme weather events. Adverse interactions between electric power generators and the natural gas system have occurred, and could occur any time of the year, because the natural gas system has been subject to interruptions that reduce the flow of natural gas to generating units requiring fuel. In addition, infrequently operated coal-fired and oil-fired generators have experienced diminished operating performance and limited energy production due to lack of fuel availability and delivery, and other physical challenges. The regional dependence on natural-gas-fired generation to provide both electric energy and capacity is expected to grow with the retirement of older coal, oil, and nuclear units and their replacement, in whole or in part, with generators in the queue that burn natural gas.

The ISO-commissioned studies of natural gas system demand scenarios quantified periods when natural-gas-fired generators may be exposed to fuel shortages. The results show that electric power generators would likely have a gas supply deficit on 24 to 34 days per winter by 2019/2020. Under 2013/2014 winter conditions, the supply deficit would be even more severe. The ISO also is participating in an EIPC study of the interregional natural gas system and its interaction with the electric power system throughout the Eastern Interconnection.

The ISO, regional stakeholders, and natural gas industry are taking other actions to mitigate the regional risks due to New England’s heavy reliance on natural gas and the limited energy-production capabilities of other resources and are implementing solutions to address fuel-adequacy issues. A fuel-reliability program and improved coordination of electric power and natural gas system operations resulted in more reliable resource performance during winter 2013/2014. A revised fuel-reliability program will be implemented for winter 2014/2015, and improvements to the day-ahead and real-time markets and the FCM currently being pursued will help achieve longer-term reliability.

Improvements to the natural gas delivery system also are under development. The New England states are considering additional means of funding new pipeline capacity into the region and are examining possible transmission infrastructure upgrades for improving the access to Canadian hydropower as an alternate source of generation. Existing efforts to coordinate interregional electric power system plans for providing greater access to resources in neighboring regions also will improve the overall reliable and economic operation of the interconnected system and enhance fuel certainty and flexibility in New England.

## State Targets for Renewable Energy

The region has significant potential for developing renewable resources and energy efficiency, encouraged by Renewable Portfolio Standards, the Regional Greenhouse Gas Initiative, and other environmental regulations and public policy objectives. In one effort, NESCOE is working with the New England states to implement a coordinated, competitive procurement of renewable resources in the region. In addition, the New England states are examining ways of increasing imports of renewable energy from Canada.

Because the states are revising their renewable resource and energy-efficiency targets to reflect different amounts and types of resources that qualify for RPSs, the ISO cannot project precise amounts for regional renewable energy targets. However, the electric energy reductions from passive demand resources, as reported in the 2014 CELT, along with the existing New England state targets for renewable resources, will meet approximately one third of New England’s total projected electric energy use by 2023. Options for meeting, or exceeding, the region’s RPS targets include developing the renewable resources in the ISO queue, importing qualified renewable resource energy from adjacent balancing authority areas, building new renewable resources in New England not yet in the queue, developing “behind-the-meter” projects, and using eligible renewable fuels in existing generators. Load-serving entities can also comply with RPS goals by making alternative compliance payments, which also serve as a cap on the price for renewable resources.

## Integration of Intermittent Resources

While intermittent resources can provide additional fuel diversity, integrating wind or solar resources could place additional stresses on the transmissions system as well as generators because system operators could call on generators to change output on short notice to provide system balancing and reserves. Wind resources have requested interconnections in remote portions of the system, which can require significant transmission upgrades. The ISO is examining improvements to the process for reviewing Elective Transmission Upgrades in the interconnection queue. To further facilitate wind integration, the ISO has incorporated wind forecasting into ISO processes, scheduling, and dispatch services and is working to implement the full economic dispatch of wind resources.

Photovoltaic resources are rapidly developing in New England and are predominately situated in southern New England. The large-scale development of photovoltaic and other distributed resources poses particularly complex issues that the ISO is beginning to address with stakeholders. The ISO cannot directly observe or control most of these resources, which may respond differently to grid disturbances than larger, conventional generators. Similar to wind resources, the large-scale integration of PV may pose challenges for system balancing and reserves.

New England is a leader in applying advanced technologies. FACTS and HVDC improve the use of transmission system infrastructure by efficiently using existing transmission system capabilities, making more efficient use of rights-of-way, and increasing the ability to move power over long distances. The ISO is using phasor measurement units to improve situational awareness and system models. Alternative technology regulation resources and active demand resources may be used to provide regulation and reserve services, which would help facilitate the reliable integration of intermittent renewable resources.

## Environmental Regulations and Initiatives

Existing and pending state, regional, and federal environmental requirements, addressing air pollution , greenhouse gas emissions, the use of cooling water from rivers and bays, and wastewater discharges into water bodies and public treatment works, will affect many New England generators in the 2015 to 2023 timeframe. When implemented, the full suite of environmental regulations, currently in various stages of promulgation, could affect generator economic performance in several ways. Generator capital costs could rise for modifying or replacing cooling systems or wastewater discharge or air pollution controls, and operating costs could increase through the increased use of new and existing pollution control devices and allowance costs. The regulations also may affect reliability by limiting generator energy production, reducing capacity output, or contributing to unit retirements. Environmental regulations affecting system performance are being monitored for their potential effects within the region and interregionally.

## Interregional Coordination

In addition to coordinating planning activities with the New England states, ISO New England proactively coordinates activities with neighboring ISO/RTO systems in the NPCC, across the Eastern Interconnection through the Eastern Interconnection Planning Collaborative, and nationally through NERC. The ISO has worked closely with NYISO and PJM to coordinate planning activities and jointly issue the 2013 Northeast Coordinated System Plan.

Sharing more supply and demand resources with other systems will likely become necessary, particularly to provide access to a greater diversity of resources, meet environmental compliance obligations, and successfully integrate intermittent resources. The ISO and the New York ISO are working toward creating a broader regional market and improving the efficiency of electricity trade between the two regions, which will improve the use of the existing ties between them. In addition to Elective Transmission Upgrades already in the interconnection queue, the New England states seek to develop additional transmission infrastructure for accommodating between 1,200 MW and 3,600 MW of net electric power imports from Québec.

## Federal, Regional, and State Initiatives

The ISO continuously works with a wide variety of state policymakers and other regional stakeholders through its planning process. Regional initiatives have improved the wholesale electricity markets, developed and integrated advanced technologies, and issued the PV forecast. The ISO has continued to provide technical support to a number of state agencies and groups, such as NECPUC, NESCOE, the New England governors, the Consumer Liaison Group, and others.

The ISO has worked with stakeholders to comply with FERC Order No. 1000 and will continue to work with stakeholders as the planning process evolves in response to FERC orders and other governmental policy developments.

## Looking Ahead

The regional energy landscape is undergoing a dramatic change in terms of the composition of generation, transmission, demand resources, and wholesale markets. This evolution poses a series of challenges the ISO is addressing through a collaborative effort of the New England states and market participants, as well as neighboring regions. Changes to the planning process and improvements to the wholesale electricity markets, which will affect the reliable and economic operation of the system, are in various stages of development. Discussions of these issues with the region’s stakeholders will be ongoing, and the ISO will provide an update on strategic planning issues and studies in RSP15.

Active involvement by all stakeholders, including public officials, state agencies, NESCOE, market participants, and other PAC members, are key elements of an open, transparent, and successful planning process. As needed, the ISO will continue to work with these groups, as well as NEPOOL, its individual members, and other interested parties, to support regional and federal policy initiatives. The ISO also will continue to provide required technical support to the New England states and the federal government as they formulate policies for the region.

# Appendix A
Acronyms and Abbreviations

| Acronym/Abbreviation | Description |
| --- | --- |
| ¢/kWh | cents per kilowatt-hour |
| $/kW-month | dollar per kilowatt-month |
| ABS | absolute value |
| AC | alternating current |
| ACP | alternative compliance payment |
| AEO | Annual Energy Outlook (EIA) |
| AGT | Algonquin Gas Transmission |
| AIM | Algonquin Incremental Market (Spectra Energy project) |
| AMI | advanced metering infrastructure |
| AMRXY | 20XY Annual Markets Report |
| Bcf; Bcf/d | billion cubic feet; billion cubic feet per day |
| BHE | 1) RSP subarea of northeastern Maine 2) Bangor Hydro Electric (Company) |
| BOSTON, BOST | RSP subarea of Greater Boston, including the North Shore (all capitalized) |
| BTA | best technology available |
| Btu | British thermal unit |
| CAA | Clean Air Act (US) |
| CAGR | compound annual growth rate |
| CAIR | Clean Air Interstate Rule |
| CC | combined cycle |
| CCP | capacity commitment period |
| CCRP | Central Connecticut Reliability Project |
| CEC | Clean Energy Center (MA) |
| CEII | critical energy infrastructure information |
| CELT | capacity, energy, loads, and transmission |
| 2013 CELT Report | 2013–2022 Forecast Report of Capacity, Energy, Loads, and Transmission |
| 2014 CELT Report | 2014–2023 Forecast Report of Capacity, Energy, Loads, and Transmission |
| CFR | Code of Federal Regulations |
| Cir. | Circuit (court) |
| CLG | Consumer Liaison Group |
| CMA/NEMA | RSP subarea comprising central Massachusetts and northeastern Massachusetts |
| CMP | Central Maine Power (Company) |
| CO2 | carbon dioxide |
| COO | chief operating officer |
| CPCN | Certificate of Public Convenience and Necessity |
| CRA | contingency reserve adjustment (factor) |
| CSAPR | Cross State Air Pollution Rule (US) |
| CSC | Cross-Sound Cable |
| CSO | capacity supply obligation |
| CT | 1) State of Connecticut 2) RSP subarea that includes northern and eastern Connecticut 3) Connecticut load zone |
| DC | direct current |
| D.C. | District of Columbia |
| D.C. Cir. | District of Columbia Circuit (US Court of Appeals) |
| DCT | double-circuit tower |
| DE | Delaware |
| DEEP | Department of Energy and Environmental Protection (CT) |
| DG | distributed generation |
| DGFWG | Distributed Generation Forecast Working Group |
| DOC | Microsoft Word file |
| DOE | Department of Energy (US) |
| DPU | Department of Public Utilities (MA) |
| Dth/d | dekatherms per day |
| DVAR | dynamic voltage ampere reactive |
| EAC | Energy Advisory Council (NH) |
| ecomin | economic minimum |
| EE | energy efficiency |
| EEF | energy-efficiency forecast |
| EIA | Energy Information Administration (US DOE) |
| EIPC | Eastern Interconnection Planning Collaborative |
| EISPC | Eastern Interconnection States Planning Council |
| ELG | Effluent Limit Guidelines (for Electric Steam Generation) (US EPA) |
| EMP | electromagnetic pulse |
| EPA | Environmental Protection Agency (US) |
| EPAct | Energy Policy Act of 2005 |
| EPRI | Electric Power Research Institute |
| ERCOT | Electric Reliability Council of Texas |
| ERO | Electric Reliability Organization |
| ETU | Elective Transmission Upgrade |
| F.3d | Federal Reporter, third series |
| FACTS | Flexible Alternating-Current Transmission System |
| FCA | Forward Capacity Auction |
| FCA #N | nth Forward Capacity Auction |
| FCM | Forward Capacity Market |
| Fed. Reg. | Federal Register |
| FERC | Federal Energy Regulatory Commission |
| fps | feet per second |
| FR | Federal Register |
| FRM | Forward Reserve Market |
| FTR | Financial Transmission Right |
| GDP | gross domestic product |
| GHCC | Greater Hartford/Central Connecticut (part of NEEWS) |
| GHG | greenhouse gas |
| GMD | geomagnetic disturbance |
| GPM | gallons per minute |
| Greater Connecticut | RSP study area that includes the RSP subareas of NOR, SWCT, and CT |
| Greater Southwest Connecticut | RSP study area that includes the southwestern and western portions of Connecticut and comprises the SWCT and NOR subareas |
| GRI | Greater Rhode Island |
| GSGT | Granite State Gas Transmission |
| GSRP | Greater Springfield Reliability Project |
| GT | gas turbine |
| GW | gigawatt |
| GWh | gigawatt-hour(s) |
| GWSA | Global Warming Solutions Act (MA) |
| HB | House Bill |
| HE | hour ending |
| HQ | Hydro-Québec Balancing Authority Area |
| HQICC | Hydro-Québec Installed Capability Credit |
| HRSG | heat-recovery steam generator |
| HRX | Housatonic River Crossing |
| (the) Hub | ISO New England energy trading hub |
| HV | high voltage |
| HVDC | high-voltage, direct current |
| ICR | Installed Capacity Requirement |
| ICU | internal combustion unit |
| IEEE | Institute of Electrical and Electronics Engineers |
| IESO | Independent Electric System Operator (Ontario, Canada) |
| IGCC | integrated combined cycle |
| IGTS | Iroquois Gas Transmission System |
| IPSAC | Inter-Area Planning Stakeholder Advisory Committee |
| IRC | ISO/RTO Council |
| IREMM | Interregional Electric Market Model |
| IRP | Interstate Reliability Project |
| ISO | Independent System Operator of New England; ISO New England |
| ISO/RTO | Independent System Operator/Regional Transmission Organization |
| ISOs | Independent System Operators |
| ISO tariff | ISO New England’s Transmission, Markets, and Services Tariff |
| IT | information technology |
| JIPC | Joint ISO/RTO Planning Committee |
| kA | kiloampere |
| kV | kilovolt(s) |
| kW | kilowatt |
| kWh | kilowatt-hour |
| lb | pound |
| LDC | local distribution company |
| LEG | limited-energy generator |
| LFG | landfill gas |
| LLC | limited liability company |
| LMP | locational marginal price |
| LNG | liquefied natural gas |
| LOLE | loss-of-load expectation |
| Lower SEMA; LSM | lower southeastern Massachusetts |
| LSE | load-serving entity |
| LSR | local sourcing requirement |
| LTRA | Long-Term Reliability Assessment (NERC) |
| M&N | Maritimes and Northeast (Pipeline) |
| MA | Massachusetts |
| MACT | maximum achievable control technology |
| MA DPU | Massachusetts Department of Public Utilities |
| MATS | Mercury and Air Toxics Standard (US EPA) |
| MCL | maximum capacity limit |
| MDth/d | thousand dekatherms per day |
| ME | 1) State of Maine 2) RSP subarea that includes western and central Maine and Saco Valley, New Hampshire 3) Maine load zone |
| MEPCO | Maine Electric Power Company, Inc. |
| METU | Market Efficiency Transmission Upgrade |
| Min Gen | Minimum Generation (Emergency) |
| MISO | Midcontinent Independent System Operator |
| MMBtu | million British thermal units |
| MMcf/d | million cubic feet per day |
| MPRP | Maine Power Reliability Program |
| MPUC | Maine Public Utilities Commission |
| MRA | market resource alternative |
| mtons | million tons |
| MVAR | megavolt-ampere reactive |
| MW | megawatt(s) |
| MWAC | the megawatts converted from the direct-current electricity produced by the photovoltaic panels to alternative current, which typically is supplied to utility customers |
| MWDC | the megawatts generated by photovoltaic panels, which produce direct-current electricity |
| MWe | electrical megawatts (of nuclear power plants) |
| MWh | megawatt-hour(s) |
| N-1 | first-contingency loss |
| N-1-1 | second-contingency loss |
| N/A | not applicable |
| NAAQS | National Ambient Air Quality Standard (US EPA) |
| NAESB | North American Energy Standards Board |
| NB | New Brunswick |
| NB–NE | New Brunswick–New England |
| NBSO | New Brunswick System Operator |
| NCPC | Net Commitment-Period Compensation |
| NCSPXY | Northeast Coordinated System Plan 20XY |
| n.d. | no date |
| NECPUC | New England Conference of Public Utilities Commissioners |
| NEEWS | New England East–West Solution |
| NEGC | New England Governors' Conference |
| NEG/ECP | New England Governors/Eastern Canadian Premiers |
| NEL | net energy for load |
| NEMA | 1) RSP subarea for northeast Massachusetts 2) Northeast Massachusetts load zone |
| NEMA/Boston | combined load zone that includes northeast Massachusetts and the Boston area |
| NEPOOL | New England Power Pool |
| NERC | North American Electric Reliability Corporation |
| NESCOE | New England States Committee on Electricity |
| NESHAP | National Emission Standard for Hazardous Air Pollutant |
| NEWIS | New England Wind Integration Study |
| NG | natural gas |
| NGA | Northeast Gas Association |
| NGCC | natural gas combined cycle |
| NH | 1) State of New Hampshire 2) RSP subarea comprising northern, eastern, and central New Hampshire; eastern Vermont; and southwestern Maine 3) New Hampshire load zone |
| NIST | National Institute of Standards and Technology |
| NJ | New Jersey |
| NMISA | Northern Maine Independent System Administrator, Inc. |
| NNE | northern New England |
| No. | number |
| NOPR | notice of proposed rulemaking |
| NOR | RSP subarea that includes Norwalk and Stamford, Connecticut |
| NOX | nitrogen oxide(s) |
| NPCC | Northeast Power Coordinating Council, Inc. |
| NPRR | nonprice retirement request |
| NPT | Northern Pass Transmission |
| NRC | Nuclear Regulatory Commission (US) |
| NREL | National Renewable Energy Laboratory (US DOE) |
| NRI | Northeast Reliability Interconnection |
| NSPS | New Source Performance Standard (US EPA) |
| NWVT | Northwest Vermont |
| NY | New York Balancing Authority Area |
| NYISO | New York Independent System Operator |
| NYPA | New York Power Authority |
| O3 | ozone |
| OATT | Open Access Transmission Tariff |
| ODR | other demand resource |
| OEP | Office of Energy and Planning (NH) |
| OER | Office of Energy Resources (RI) |
| OP 4 | ISO Operating Procedure No. 4, Action during a Capacity Deficiency |
| OP 7 | ISO Operating Procedure No. 7, Action in an Emergency |
| OP 8 | ISO Operating Procedure No. 8, Operating Reserve and Regulation |
| OP 19 | ISO Operating Procedure No. 19, Transmission Operations |
| PA | Pennsylvania |
| PAC | Planning Advisory Committee |
| PAR | phase-angle regulator |
| PDC | phasor data concentrator |
| PDF | Adobe Portable Document Format file |
| PFP | pay for performance |
| PJM | PJM Interconnection LLC; the RTO for all or parts of Delaware, Illinois, Indiana, Kentucky, Maryland, Michigan, New Jersey, North Carolina, Ohio, Pennsylvania, Tennessee, Virginia, and the District of Columbia |
| PM | particulate matter |
| PM2.5 | fine particulate matter |
| PMU | phasor measurement unit |
| PNGTS | Portland Natural Gas Transmission System |
| pnode | pricing node |
| PP 10 | ISO Planning Procedure No. 10, Planning Procedure to Support the Forward Capacity Market |
| PPT | Microsoft PowerPoint file |
| PSERC | Power System Engineering Research Center (US DOE) |
| PSNH | Public Service of New Hampshire |
| PSPC | Power Supply Planning Committee |
| PTF | pool transmission facility |
| PTO | participating transmission owner |
| Pub. L. | public law |
| PUC | Public Utilities Commission |
| PURA | Public Utilities Regulatory Authority (CT) |
| PV | photovoltaic |
| QER | Quadrennial Energy Review (US DOE) |
| queue (the) | ISO Generator Interconnection Queue |
| RC | Reliability Committee |
| REC | Renewable Energy Certificate |
| REMVEC | Rhode Island-Eastern Massachusetts-Vermont Energy Control |
| RES | Renewable Energy Standard |
| RFC | ReliabilityFirst Corporation |
| RFP | request for proposals |
| RGGI | Regional Greenhouse Gas Initiative |
| RGSP | real gross state product |
| RI | 1) State of Rhode Island 2) RSP subarea that includes the part of Rhode Island bordering Massachusetts 3) Rhode Island load zone |
| RIRP | Rhode Island Reliability Project |
| RNS | Regional Network Service |
| ROS | Rest-of-System (reserve zone) |
| ROSE | Region of Stability Existence |
| RPS | Renewable Portfolio Standard |
| RSP | Regional System Plan |
| RSPXY | 20XY Regional System Plan |
| RTDR | real-time demand response |
| RTEG | real-time emergency generation |
| RTO | Regional Transmission Organization |
| S&D | Scheduling System Control and Dispatch Service Rate |
| SB | Senate Bill |
| SBC | systems benefits charge |
| SCC | seasonal claimed capability |
| SCR | selective catalytic reduction |
| SDNY | US District Court Southern District of New York |
| SEC | Site Evaluation Committee (NH) |
| SEMA | 1) RSP subarea comprising southeastern Massachusetts and Newport, Rhode Island 2) Southeastern Massachusetts load zone |
| SGIP | small generator interconnection procedure |
| SMD | Standard Market Design |
| SME | RSP subarea for southeastern Maine |
| SO2 | sulfur dioxide |
| SOEP | Sable Offshore Energy Project |
| SPI | Strategic Planning Initiative |
| SPS | special protection system |
| SSC | Stakeholder Steering Committee (EIPC) |
| SSCC | summer seasonal claimed capability |
| STATCOM | static synchronous compensator |
| SVC | static voltage ampere reactive (VAR; V) compensator |
| SWCT | RSP subarea for southwestern Connecticut |
| tbd | to be determined |
| tcf | trillion cubic feet |
| TC | Transmission Committee |
| TCSC | thyristor-controlled series compensation |
| TGP | Tennessee Gas Pipeline |
| TMNSR | 10-minute nonspinning reserve |
| TMOR | 30-minute operating reserve |
| TMSR | 10-minute spinning reserve |
| TQM | Trans-Québec and Maritimes (pipeline) |
| TVA | Tennessee Valley Authority |
| US | United States |
| USC | United States Code |
| VAR | voltage ampere reactive |
| VER | variable energy resource |
| VELCO | Vermont Electric Power Company |
| VSC | voltage source converter |
| VT | 1) State of Vermont 2) RSP subarea that includes Vermont and southwestern New Hampshire 3) Vermont load zone |
| VY | Vermont Yankee |
| WCMA | Western/Central Massachusetts load zone |
| WIP | Wright Interconnection Project (of the Iroquois Gas Transmission System) |
| WMA | RSP subarea for western Massachusetts |
| WMPP | Wholesale Markets Project Plan |
| XLS | Microsoft Excel file |
| yr | year |

The requirements of the OATT, which include Attachment K, the ISO Information Policy, and interconnection procedures, address generator and elective upgrades. ISO New England Inc. Transmission, Markets, and Services Tariff (ISO tariff), Section II, Open Access Transmission Tariff, Attachment K, “Regional System Planning Process,” http://www.iso-ne.com/regulatory/tariff/sect_2/oatt/sect_ii.pdf. ISO tariff, Attachment D, “ISO New England Information Policy,” http://www.iso-ne.com/static-assets/documents/regulatory/tariff/attach_d/attachment_d.pdf.

RSP14 is based on the June 2014 RSP Project List (XLS file), http://www.iso-ne.com/system-planning/system-plans-studies/rsp.

The NEPOOL stakeholder process provides advisory input on market, reliability, tariff, and OATT matters; however, the primary forum for regional system planning is the ISO’s Planning Advisory Committee (PAC). More information is available at http://www.iso-ne.com/committees/participants/participants-committee and http://www.iso-ne.com/committees/planning/planning-advisory.

Past RSPs are archived at http://www.iso-ne.com/trans/rsp/index.html. For access to supporting reports, contact ISO Customer Service at 413-540-4220.

Supporting information and some supplements to the RSP statistics, such as import and export figures, are available at New England 2014 Regional System Plan (RSP14) Load, Energy and Capacity Resource Overview (April 29, 2014), http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/mtrls/2014/apr292014/a4_rsp14_load_and_capacity_resource_overview.pdf.

The mix of capacity resources could change. Updates are included in the ISO’s monthly chief operating officer (COO) report to the NEPOOL Participants Committee; http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/prtcpnts/mtrls/index.html.

PAC materials and meeting minutes are available at http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/index.html. For access to PAC critical energy infrastructure information (CEII), complete the PAC Access Request Form at http://www.iso-ne.com/participate/support/request-information and mail to ISO New England Inc., Attn: Customer Support, One Sullivan Road, Holyoke, MA 01040-2841, or email the PDF file to custserv@iso-ne.com.

A demand resource is a capacity product, type of equipment, system, service, practice, or strategy that verifiably reduces end-use demand for electricity from the power system.

Meeting materials, notes, and meeting dates for discussing the Strategic Planning Initiative are available at http://www.iso-ne.com/committees/comm_wkgrps/strategic_planning_discussion/index.html.

PAC materials and meeting minutes are available at http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/index.html. For access to PAC critical energy infrastructure information (CEII), complete the PAC Access Request Form at http://www.iso-ne.com/participate/support/request-information and mail to ISO New England Inc., Attn: Customer Support, One Sullivan Road, Holyoke, MA 01040-2841, or email the PDF file to custserv@iso-ne.com.

ISO New England Inc. Transmission, Markets, and Services Tariff (ISO tariff), Section II, Open Access Transmission Tariff, http://www.iso-ne.com/regulatory/tariff/sect_2/oatt/sect_ii.pdf. More information on NEPOOL is available at http://www.iso-ne.com/committees/participants/participants-committee.

FERC, Order on Compliance Filings (May 17, 2013), http://www.iso-ne.com/static-assets/documents/regulatory/ferc/orders/2013/may/er13_193_er13_196_5_17_13_order_on_order_1000_compliance_filings.pdf. “Transmission Operating Agreements,” webpage, http://www.iso-ne.com/static-assets/documents/regulatory/ferc/orders/2013/may/er13_193_er13_196_5_17_13_order_on_order_1000_compliance_filings.pdf.

ISO tariff (2014), http://www.iso-ne.com/regulatory/tariff/index.html.

Information on NERC requirements is available at http://www.nerc.com. Information on NPCC is available at http://www.npcc.org/. An NPCC compliance audit conducted from March 12 through March 15, 2012, showed no ISO violations of any standards and requirements.

ISO tariff Section II, Open Access Transmission Tariff, Attachment K, “Regional System Planning Process” (January 1, 2014), http://www.iso-ne.com/regulatory/tariff/sect_2/oatt/sect_ii.pdf.

A load pocket is an area of the system that requires local generation to meet demand because the transfer capability of the transmission system is insufficient to serve the load in that area.

The Eastern Interconnection consists of the interconnected transmission and distribution infrastructure that synchronously operates east of the Rocky Mountains, excluding the portion of the system located in the Electric Reliability Council of Texas (ERCOT), Newfoundland, Labrador, and Québec.

A distributed generation resource is generation provided by a relatively small, on-site installation directly connected to a distribution facility or retail customer facility and not the regional power system (i.e., it is “behind the meter”), which can alleviate or prevent regional power system transmission or distribution constraints or reduce or eliminate the need to install new transmission or distribution facilities. A small (24 kilowatt) solar photovoltaic system installed by a retail customer is an example of distributed generation.

“Status of Nonprice Retirement Requests,” webpage, http://www.iso-ne.com/genrtion_resrcs/reports/sts_non_retrmnt_rqst/. An existing resource can submit a delist bid for opting out of the capacity market for one year or permanently if the Forward Capacity Auction were to fall below a certain price. Several types of delist bids exist. A nonprice retirement request is an irrevocable request to retire all or a portion of a resource. This type of request, which supersedes any delist bids submitted, is subject to a review for reliability impacts. If the ISO notifies a resource owner of a reliability need for the resource, the resource owner has the option to retire the resource as requested or continue to operate it until the reliability need has been met, after which the resource must retire. For more information on delist bids and nonprice retirement requests, refer to the ISO’s Overview of New England's Wholesale Electricity Markets and Market Oversight (May 6, 2014), http://www.iso-ne.com/static-assets/documents/pubs/spcl_rpts/2014/2014_market_overview_050614.pdf.

The ISO’s Generator Interconnection Queue includes the requests that generators submit to ISO New England to interconnect to the ISO-administered transmission system.

The FCM reconfiguration auctions take place before and during the capacity commitment period (i.e., June 1 through May 31 of the following year) to allow participants to buy and sell capacity obligations and adjust their positions.

Information on the January 2004 cold snap is available in the 2005 Regional System Plan, Section 5.1.2, at https://smd.iso-ne.com/trans/sys_studies/rsp_docs/rpts/2005/102005_RSP05_Final.pdf. Section 6.2.2 of this report contains additional details on 2013/2014 winter natural gas supply constraints. Also refer to the ISO’s 2013 Annual Markets Report (AMR13), Section 2.1.3.4 (May 6, 2014), http://www.iso-ne.com/markets/mkt_anlys_rpts/annl_mkt_rpts/2013/2013_amr_final_050614.pdf.

ICF International, Assessment of New England’s Natural Gas Pipeline Capacity to Satisfy Short and Near-Term Electric Generation Needs: Phase II, PAC presentation (December 18, 2013), http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/mtrls/2013/dec182013/a3_draft_icf_phase_2_gas_study_report_without_appendices.pdf.

A planned outage is the scheduled inoperability of a generator, generally to perform maintenance. A forced outage is a type of unplanned outage that involves the unexpected removal from service of a generating unit, transmission facility, or other facility or portion of a facility due to an emergency failure or the discovery of a problem that needs to be repaired as soon as any combination of crews, equipment, or corrective dispatch actions can be put in place to allow the work to be performed.

An Elective Transmission Upgrade is an upgrade or interconnection to the pool transmission facilities that are part of the New England transmission system, voluntarily funded by an entity or entities that have agreed to pay for all the costs of the upgrade.

Strategic Transmission Analysis: Wind Integration Study—Stage 1—Maine, Regional Constraints, PAC presentation (May 21, 2014), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2014/may212014/a4_strategic_transmission_analysis_wind_power_update.pdf (STA Wind Integration Study, 2014). ISO New England, 2011 Economic Study (March 31, 2014), http://www.iso-ne.com/static-assets/documents/committees/comm_wkgrps/prtcpnts_comm/pac/reports/2014/2011_eco_study_final.pdf. 2012 Economic Study (April 2014), http://www.iso-ne.com/static-assets/documents/committees/comm_wkgrps/prtcpnts_comm/pac/reports/2014/a9_2012_economic_study_final.pdf.

FERC, Order Accepting Tariff Revisions, (September 9, 2014), http://www.iso-ne.com/static-assets/documents/2014/09/er14-2407-000_9-9-14_order_accept_winter_reliability.pdf.

PJM Interconnection LLC is the RTO for all or parts of Delaware, Illinois, Indiana, Kentucky, Maryland, Michigan, New Jersey, North Carolina, Ohio, Pennsylvania, Tennessee, Virginia, West Virginia, and the District of Columbia. Additional information on the EIPC is available at http://www.eipconline.com/.

ISO New England, Order No. 1000 Interregional Compliance Filing of ISO New England Inc. and the Participating Transmission Owners Administrative Committee, Supported by the New England Power Pool Participants Committee, FERC filing (July 10, 2013), http://www.iso-ne.com/static-assets/documents/regulatory/ferc/filings/2013/jul/er13_1960_000_7_10_2013_order_1000.pdf.

The 50/50 “reference-case” peak loads have a 50% chance of being exceeded because of weather conditions. For the reference case, the summer peak load is expected to occur at a weighted New England-wide temperature of 90.2°F, and the winter peak load is expected to occur at 7.0°F. The 90/10 peak loads have a 10% chance of being exceeded because of weather. For the 90/10 case, the summer peak is expected to occur at a temperature of 94.2°F, and the winter peak is expected to occur at a temperature of 1.6°F.

The actual load has been near or above the 50/50 forecast 11 times during the last 21 years because of weather conditions; six of these 11 times, the load has been near or has exceeded the 90/10 forecast.

The ISO’s Forecast Data 2014 (April 30, 2014), XLS file, worksheet 9 (http://www.iso-ne.com/static-assets/documents/trans/celt/fsct_detail/2014/isone_fcst_data_2014.xls) shows that the gross consumption of electric energy for 2023 is 151,525, gigawatt-hours (GWh). The savings attributable to federal appliance standards is 2,506 GWh for 2023. In addition, passive demand resources are projected to save 20,967 GWh for 2023 (see worksheet 2).

Passive demand resources reduce electric energy consumption that otherwise would have been served by generation resources and include such resources as energy efficiency and distributed generation in locations that have net metering. Active demand resources (i.e., demand response) reduce load in response to a request from the ISO for system reliability reasons or in response to a price signal. Net metering allows power customers who generate their own electricity, such as from wind or solar power, to feed their unused electricity back into the grid.

ISO New England Energy-Efficiency Forecast Report for 2018 to 2023 (June 3, 2014), http://www.iso-ne.com/static-assets/documents/2014/08/eef_report_2018_2023_final.pdf.

The 34,195 MW 90/10 gross load for 2023 minus the 3,322 MW peak EE savings for 2023 equals the 30,873 MW net for 2023, which is 747 MW less than the 31,620 MW 50/50 gross forecast for 2023.

The nameplate value of a PV installation is the maximum rated output of the equipment. In general, the nameplate rating is a measure of a piece of equipment’s ability to produce or transmit electricity.

Seasonal claimed capability is a generator's maximum production or output during a particular season, adjusted for physical and regulatory limitations. The actual value that the ISO uses in studies and the markets may vary from this number.

The net ICR values for 2014/2015 to 2017/2018 are the latest values approved by FERC and are available at http://www.iso-ne.com/system-planning/resource-planning/installed-capacity-requirements. Representative net ICR values are illustrative future ICRs for the region, minus a monthly value that reflects the annual installed capacity benefits of the Hydro Québec Phase II Interconnection.

OP 4 actions include allowing the depletion of the 30-minute and partial depletion of the 10-minute reserves (1,000 MW) (see Section 4.3), scheduling market participants’ submitted emergency transactions and arranging emergency purchases between balancing authority areas (1,600 to 2,000 MW), and implementing 5% voltage reductions (400 to 450 MW). Operating Procedure No. 4, Action during a Capacity Deficiency (December 9, 2011), http://www.iso-ne.com/static-assets/documents/rules_proceds/operating/isone/op4/op4_rto_final.pdf.

Higher tie-reliability benefits and reductions in the net ICR would increase the frequency and depth of OP 4 actions.

FCA #8 covers June 1, 2017, through May 31, 2018. Existing capacity resources are required to participate in the FCA and automatically are entered into the capacity auction. However, these resources may indicate a desire to be removed from the FCA by submitting a delist bid before the existing-capacity qualification deadline.

Of this total, 2,431 MW consisted of five resources representing 1,535 MW from the Brayton Point Station, three resources representing 342 MW from Norwalk Harbor Station, and 554 MW of demand-response resources. Static delist bids for a resource must be submitted before the existing capacity qualification deadline, which occurs approximately eight months before an FCA. These delist bids are for resources opting to remove all or part of their total capacity from the market for a single commitment period at a price greater than or equal to $1.00/kW-month.

A local sourcing requirement is the minimum amount of capacity that must be electrically located within an import-constrained capacity zone to meet the ICR.

The Capacity Carry Forward Rule addresses situations where a large resource meets a zonal need but eliminates any need for new resources in the subsequent auction (Market Rule 1, Section III.13.2.7.9). In the NEMA/Boston capacity zone, the Capacity Carry Forward Rule was triggered when a new source cleared in FCA #7, such that other new resources were not needed in subsequent FCAs.

FERC, Order on Compliance Filing (May 31, 2013), http://www.iso-ne.com/static-assets/documents/regulatory/ferc/orders/2013/may/er12_953_002_5_31_13_order_accept_fcm_compliance.pdf.

The retirement of Brayton Point Station (1,535 MW) could trigger the need for modeling a Southeast Massachusetts/Rhode Island capacity zone in FCA #9.

According to NERC, NPCC, and ISO criteria, a contingency is the loss of one or more generation, transmission, or both types of facilities or power system elements. A system’s first contingency (N-1) is when the power element (facility) with the largest impact on system reliability is lost. A second contingency (N-1-1) takes place after a first contingency has occurred and is the loss of the facility that at that time has the largest impact on the system.

Spinning operating reserves are on-line resources that can increase output. Nonsynchronized (i.e., nonspinning) operating reserves are off-line resources that can be electrically synchronized to the system quickly, reaching maximum output within 10 to 30 minutes.

To conduct some RSP studies, the region is divided into various areas associated with their electrical system characteristics. Greater Connecticut is an area that has boundaries similar to the State of Connecticut but is slightly smaller because of electrical system limitations near Connecticut’s borders with western Massachusetts and Rhode Island. Greater Southwest Connecticut includes southwestern and western portions of Connecticut. The BOSTON area (all capitalized) includes the city of Boston and northeast Massachusetts (see Section 2.4).

Regional network service is the transmission service over the pool transmission facilities (PTFs), including services used for network resources or regional network load not physically interconnected with a PTF.

Cost estimates without transmission cost allocation approval are subject to established variations as projects progress through various stages of implementation. The $4.5 billion cost estimate has a range of $3.7 to $5.3 billion based on projects proposed, planned, and under construction. See the Regional System Plan Transmission Projects June 2014 Update, PAC presentation (June 19, 2014), slide 12, at http://www.iso-ne.com/static-assets/documents/committees/comm_wkgrps/prtcpnts_comm/pac/mtrls/2014/jun192014/a5_rsp14_project_list_update_final.zip.

The results of a study of the changes in transfer limits across major interactions in Maine, including Maine to New Hampshire, is available at Maine Power Reliability Program (MPRP): Transfer Capability Study Results, PAC presentation (December 13, 2012), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2012/dec132012/mprp_transfer_limits.pdf. Also see MPRP North to South Steady State Transfer Limits and Incremental Stability Performance Study, final draft report (November 2012), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/reports/2012/mprp_transfer_limits.pdf.

While natural gas units are generally in merit, the price of natural gas can spike relative to other fuels, as happened during the winter 2013/2014.

Market Rule 1, http://www.iso-ne.com/regulatory/tariff/sect_3/index.html. The ISO’s AMR13, Section 2.1.4, contains additional information on the limited-energy generation provisions; http://www.iso-ne.com/static-assets/documents/markets/mkt_anlys_rpts/annl_mkt_rpts/2013/2013_amr_final_050614.pdf.

FERC, Order Conditionally Accepting Tariff Revisions (September 16, 2013), http://www.iso-ne.com/regulatory/ferc/orders/2013/sep/er13-1851-000_9-16-2013_winter_rel.pdf.

ISO New England Inc., Docket No. ER14-___-000, Winter 2014-15 Reliability Program (Parts 1 and 2), FERC filing (July 11, 2014), http://www.iso-ne.com/static-assets/documents/regulatory/ferc/filings/2014/jul/er14_2407_000_win_rel_pro_7_11_2014.pdf and http://www.iso-ne.com/regulatory/ferc/filings/2014/jul/er14-2407-001_winter_rel_7-11-2014.pdf. Also see above footnote for FERC’s September 10, 2014, order.

The Energy Market Offer Flexibility Rule will allow power supply offers to vary by hour in the Day-Ahead Energy Market, changes in Real-Time Energy Market bids until 30 minutes before the hour in which the offer applies, and negative offers in both markets as low as −$150/MWh. For additional information on these market improvements, see the ISO’s “Interdependencies of Market and Operational Changes to Address Resource Performance and Gas Dependency” (2013), http://www.iso-ne.com/committees/comm_wkgrps/strategic_planning_discussion/materials/interdependency_of_iso_proposals_to_key_spi_risks.pdf. Also, ISO New England Inc. and New England Power Pool, Energy Market Offer Flexibility Changes, FERC filing (July 1, 2013), http://www.iso-ne.com/static-assets/documents/regulatory/ferc/filings/2013/jul/er13_1877_000_mkt_offer_flex_7_1_2013.pdf.

ICF International, Assessment of New England’s Natural Gas Pipeline Capacity to Satisfy Short- and Near-Term Electric Generation Needs, final report (June 15, 2012), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/reports/2012/gas_study_ceii.pdf.

2012 ISO New England Electric Generator Air Emissions Report (January 2014), http://www.iso-ne.com/static-assets/documents/genrtion_resrcs/reports/emission/2012_emissions_report_final_v2.pdf. These changes in generation are consistent with New England fuel consumption in 2011 and 2012, as reported by the US Energy Information Administration (EIA). Coal consumption for electric generators fell from 3.0 million short tons in 2011 to 1.8 million short tons in 2012, and residual fuel oil consumption fell from 0.7 million barrels in 2011 to 0.3 million barrels in 2012.

In all communications, the ISO must adhere to the requirements of its Information Policy regarding the disclosure of confidential information. ISO New England Information Policy (ISO tariff, Attachment D) (2014), http://www.iso-ne.com/static-assets/documents/regulatory/tariff/attach_d/attachment_d.pdf.

Renewable Energy Certificates are tradable, nontangible commodities, each representing the eligible renewable generation attributes of 1 MWh of actual generation from a grid-connected renewable resource.

ISO New England, Wind Development in Constrained Areas, PAC presentation (March 21, 2013), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2013/mar212013/a5_wind_development_in_constrained_areas_new.pdf, and the STA Wind Integration Study (2014).

2011 Economic Study, http://www.iso-ne.com/static-assets/documents/committees/comm_wkgrps/prtcpnts_comm/pac/reports/2014/2011_eco_study_final.pdf.

2012 Economic Study, http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/reports/2014/a9_2012_economic_study_final.pdf.

The Hub is a collection of 32 electric energy pricing locations in central New England where little congestion is evident.

Market Resource Alternative Analysis—Demand-Side Results Greater Hartford and Central Connecticut Area, PAC presentation (November 14, 2012), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2012/nov142012/ghcc_mra_november.pdf, and Market Resource Alternative Analysis —Final Supply-Side Results Greater Hartford and Central Connecticut Area, PAC presentation (December 13, 2012), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2012/dec132012/ghcc_mra.pdf.

ISO New England, NYISO, PJM, 2013 Northeast Coordinated System Plan (April 16, 2014), http://www.iso-ne.com/static-assets/documents/committees/comm_wkgrps/othr/ipsac/mtrls/2014/mar282014/2013_ncsp.pdf. The protocol and supplemental materials and reports are available at http://www.iso-ne.com/committees/planning/ipsac.

ISO New England, Transmission Planning Process Guide, draft (February 5, 2013), http://www.iso-ne.com/static-assets/documents/committees/comm_wkgrps/prtcpnts_comm/pac/plan_guides/plan_process_guide/planning_process_guide_for_february_pac_2_5_2013__3_.docx; Transmission Planning Technical Guide, draft (December 6, 2013), http://www.iso-ne.com/static-assets/documents/committees/comm_wkgrps/prtcpnts_comm/pac/plan_guides/plan_tech_guide/planning_technical_guide_clean_12_06_2013.pdf.

Likewise, the markets and market changes may help meet future system needs by providing incentives for the development of new resources. Market changes are subject to a different stakeholder process and are described in the ISO’s Annual Markets Report (AMR) (accessible at http://www.iso-ne.com/markets-operations/market-monitoring-mitigation/internal-monitor) and Wholesale Markets Project Plan (WMPP) (http://www.iso-ne.com/markets-operations/markets-development/wholesale-markets-project-plan).

ISO New England Inc. Transmission, Markets, and Services Tariff (ISO tariff) (2014), http://www.iso-ne.com/regulatory/tariff/index.html, including Section II. ISO New England Open Access Transmission Tariff, http://www.iso-ne.com/regulatory/tariff/sect_2/oatt/sect_ii.pdf.

A balancing authority area is a group of generation, transmission, and loads within the metered boundaries of the entity (balancing authority) that maintains the load-resource balance within the area. The Eastern Interconnection consists of the interconnected transmission and distribution infrastructure that synchronously operates east of the Rocky Mountains, excluding the portion of the system located in the Electric Reliability Council of Texas (ERCOT) and Québec.

A demand resource is a capacity product, type of equipment, system, service, practice, or strategy that verifiably reduces end-use demand for electricity from the power system. Active demand resources (i.e., demand response) reduce load quickly or continuously in response to a request from the ISO for system reliability reasons or in response to a price signal. Passive demand resources are nondispatchable resources that reduce electric energy consumption that generation resources would have otherwise served and include energy-efficiency measures and “behind-the meter” (on-site) distributed generation (DG) in locations that have net metering (see more on DG below). Net metering allows power customers who generate their own electricity, such as from wind or solar power, to feed their unused electricity back into the grid.

An Elective Transmission Upgrade is required for interconnecting a merchant transmission facility to the ISO system. A merchant transmission facility is an independently developed and funded facility subject to the operational control of the ISO, pursuant to an operating agreement specific to each facility (refer to Section 5.2.4).

ISO New England, Transmission Planning Process Guide, draft, http://www.iso-ne.com/static-assets/documents/committees/comm_wkgrps/prtcpnts_comm/pac/plan_guides/plan_process_guide/planning_process_guide_for_february_pac_2_5_2013__3_.docx. Transmission Planning Technical Guide, draft, http://www.iso-ne.com/static-assets/documents/committees/comm_wkgrps/prtcpnts_comm/pac/plan_guides/plan_tech_guide/planning_technical_guide_clean_12_06_2013.pdf.

FERC, ISO New England Inc. Order on Compliance Filings (May 17, 2013), http://www.iso-ne.com/regulatory/ferc/orders/2013/may/er13-193_er13-196_5-17_13_order_on_order_1000_compliance_filings.pdf. Also see “Order No. 1000—Transmission Planning and Cost Allocation,” FERC webpage (updated May 17, 2013), http://www.ferc.gov/industries/electric/indus-act/trans-plan.asp.

A distributed generation resource is generation provided by a relatively small, on-site installation directly connected to a distribution facility or retail customer facility and not the regional power system (i.e., it is “behind the meter”), which can alleviate or prevent regional power system transmission or distribution constraints or reduce or eliminate the need to install new transmission or distribution facilities. A small (24 kilowatt) photovoltaic system installed by a retail customer is an example of distributed generation.

Refer to the OATT, Attachment K, Section 4.1 and 4.2 for complete definitions for needs assessments and solutions studies; http://www.iso-ne.com/regulatory/tariff/sect_2/oatt/sect_ii.pdf.

Any stakeholder can designate a representative to the PAC by providing written notice to the ISO. PAC materials (2001–2014) are available at http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/index.html. PAC agendas; minutes; materials; draft reports, including stakeholder questions and ISO responses; and final reports are posted on the ISO website.

NEPOOL members serve as ISO stakeholders and market participants. More information on NEPOOL participants is available at http://www.iso-ne.com/participate/governing-agreements/nepool-agreement.

A Transmission Operating Agreement is an agreement between a Regional Transmission Operator and a transmission-providing utility whereby the RTO pays the utility for its transmission system costs in exchange for control of the transmission.

Market Rule 1 (ISO tariff, Section III) (2014), http://www.iso-ne.com/regulatory/tariff/sect_3/index.html.

The current list is available at http://www.iso-ne.com/system-planning/system-plans-studies/rsp (filters: Regional System Plan document type; XLS file type).

Recent and archived RSP materials are available at http://www.iso-ne.com/trans/rsp/index.html. The latest and archived editions of the AMR are available at http://www.iso-ne.com/markets/mkt_anlys_rpts/annl_mkt_rpts/. The latest and archived WMPPs are available at http://www.iso-ne.com/markets-operations/markets-development/wholesale-markets-project-plan. The needs assessments and solutions studies presented to the PAC and posted on the ISO website can be obtained by contacting ISO Customer Service at 413-540-4220.

Stakeholders also can obtain publicly available models of the transmission system network through the FERC 715 process, which requires transmitting utilities that operate facilities rated at or above 100 kilovolts (kV) to submit information to FERC annually; see http://www.ferc.gov/docs-filing/forms/form-715/overview.asp. ISO New England Information Policy (ISO tariff, Attachment D) (2014) contains the requirements for controlling the disclosure of CEII and confidential information; see http://www.iso-ne.com/static-assets/documents/regulatory/tariff/attach_d/attachment_d.pdf.

ISO New England, “Rules and Procedures” webpage, http://www.iso-ne.com/participate/rules-procedures. FERC, Preventing Undue Discrimination and Preference in Transmission Service, 18 CFR Parts 35 and 37, Order No. 890 (February 16, 2007), http://www.ferc.gov/whats-new/comm-meet/2007/021507/E-1.pdf. NERC Reliability Standards (2013), http://www.nerc.com/page.php?cid=2|20. NPCC Regional Standards (2012), https://www.npcc.org/Standards/default.aspx. Also see Sections 7.1.4.

“Transmission Operating Agreements” webpage, http://www.iso-ne.com/regulatory/toa/index.html.

Order No. 1000 Interregional Compliance Filing of ISO New England Inc. and the Participating Transmission Owners Administrative Committee, Supported By the New England Power Pool Participants Committee (July 10, 2013), http://www.iso-ne.com/regulatory/ferc/filings/2013/jul/er13-1960-000_7-10-2013_order_1000.pdf. Filing of Amended and Restated Northeastern ISO/RTO Planning Coordination Protocol on behalf of ISO New England Inc., New York Independent System Operator, Inc., and PJM Interconnection, L.L.C. (July 10, 2013), http://www.iso-ne.com/regulatory/ferc/filings/2013/jul/er13-1957-000_7-10-2013_protocol.pdf. Further Order No. 1000 Regional Compliance Filing of ISO New England Inc. and the Participating Transmission Owners Administrative Committee, FERC filing (both sets of amendments and cover letter) (November 15, 2013), http://www.iso-ne.com/static-assets/documents/regulatory/ferc/filings/2013/nov/er13_196_002_11_15_2013_order_1000.pdf and http://www.iso-ne.com/static-assets/documents/regulatory/ferc/filings/2013/nov/er13_193_003_11_15_2013_order_1000.pdf. FERC, “Transmission Planning and Cost Allocation,” webpage, http://www.ferc.gov/industries/electric/indus-act/trans-plan.asp.

The ISO is not responsible for portions of northern and eastern Maine. The Northern Maine Independent System Administrator, Inc. (NMISA) is a nonprofit entity responsible for the administration of the northern Maine transmission system and electric power markets in Aroostook and Washington counties. The 2014 peak load forecast for NMISA is approximately 122 MW.

For more information on New England wholesale electricity markets, see the ISO’s 2013 Annual Markets Report (AMR13) (May 6, 2014), http://www.iso-ne.com/static-assets/documents/markets/mkt_anlys_rpts/annl_mkt_rpts/2013/2013_amr_final_050614.pdf, and an Overview of New England’s Wholesale Electricity Markets and Market Oversight (Markets Overview Report) (May 6, 2014), http://www.iso-ne.com/static-assets/documents/pubs/spcl_rpts/2014/2014_market_overview_050614.pdf.

Installed capacity is the megawatt capability of a generating unit, dispatchable load, external resource or transaction, or demand resource that qualifies as a participant in the ISO’s Forward Capacity Market according to the market rules. Additional information is available at http://www.iso-ne.com/markets-operations/markets/forward-capacity-market.

Regulation is the capability of specially equipped generators to increase or decrease their generation output every four seconds in response to signals they receive from the ISO to control slight changes on the system.

According to NERC, NPCC, and ISO criteria, a contingency is the sudden loss of a generation or transmission resource. A system’s first contingency (N−1) is when the power element (facility) with the largest impact on system reliability is lost. A second contingency (N−1−1) takes place after a first contingency has occurred and is the loss of the facility that at that time has the largest impact on the system. A forced outage is a type of unplanned outage that involves the unexpected removal from service of a generating unit, transmission facility, or other facility or portion of a facility due to an emergency failure or the discovery of a problem that needs to be repaired as soon as any combination of crews, equipment, or corrective dispatch actions can be put in place to allow the work to be performed.

Fast-start resources can be electrically synchronized to the system quickly and reach claimed capability (i.e., a generator’s maximum production or output) within 10 to 30 minutes to respond to a contingency and serve demand.

The ISO tariff allows loads that meet specified requirements to request and receive nodal pricing.

See Market Rule 1, Section III.2.7, of the ISO tariff, http://www.iso-ne.com/participate/rules-procedures/tariff/market-rule-1.

FERC, ISO New England Inc. Order Accepting Compliance Filing (issued April 28, 2014), http://www.iso-ne.com/regulatory/ferc/orders/2014/apr/er12-953-004-4-28-14_order_accept_cap_zone_compliance.pdf.

RTDRs are demand resources that must curtail electrical usage within 30 minutes of receiving a dispatch instruction from the ISO. Real-time emergency generation is distributed generation the ISO calls on to operate during certain voltage-reduction or more severe actions but must limit its operation to 600 MW to comply with the generation’s federal, state, or local air quality permit(s), as well as the ISO’s market rules. RTEG operations result in curtailing load on the grid, as the distributed energy provided by the emergency generator begins serving demand.

The ISO’s Capacity, Energy, Load, and Transmission (CELT) Reports and associated documentation contain more details on the short-run and long-run forecast methodologies, models, and inputs; weather normalization; regional, state, subarea, and load-zone forecasts of annual electric energy use and peak loads; high- and low-forecast bandwidths; and retail electricity prices. They are available at the “CELT Reports,” webpage, http://www.iso-ne.com/system-planning/system-plans-studies/celt. Also see the 2014 CELT Report (http://www.iso-ne.com/static-assets/documents/trans/celt/report/2014/2014_celt_report_rev.pdf) and the ISO NE Seasonal Peaks since 1980 (April 22, 2014), which can be accessed at the “Energy, Load, and Demand Reports,” webpage, http://www.iso-ne.com/isoexpress/web/reports/load-and-demand/-/tree/net-ener-peak-load.

The 50/50 “reference” case peak loads have a 50% chance of being exceeded because of weather conditions. For the reference case, the summer peak load is expected to occur at a weighted New England-wide temperature of 90.2°F, and the winter peak load is expected to occur at 7.0°F. The 90/10 “extreme” case peak loads have a 10% chance of being exceeded because of weather. For the extreme case, the summer peak is expected to occur at a temperature of 94.2°F, and the winter peak is expected to occur at a temperature of 1.6°F.

Preliminary ISO-NE Annual Energy and Seasonal Peak Forecast 2014–2023, PAC presentation (Preliminary Forecast 2014–2023) (February 19, 2014), http://www.iso-ne.com/static-assets/documents/committees/comm_wkgrps/prtcpnts_comm/pac/mtrls/2014/feb192014/a7_preliminary_iso_load_forecast_2014_2023.pdf.

Energy-only generators are considered part of the generation output within the area.

The compound annual growth rate (CAGR) is calculated as follows:

Preliminary Forecast 2014–2023 presentation, slide 22 (http://www.iso-ne.com/static-assets/documents/committees/comm_wkgrps/prtcpnts_comm/pac/mtrls/2014/feb192014/a7_preliminary_iso_load_forecast_2014_2023.pdf).

OP 4 actions implemented during a capacity deficiency include Action 2, the dispatch of real-time demand resources, and Action 6, the dispatch of real-time emergency generation. Operating Procedure No. 4, Action during a Capacity Deficiency (October 5, 2013), http://www.iso-ne.com/static-assets/documents/rules_proceds/operating/isone/op4/op4_rto_final.pdf.

Weather conditions during the actual peak summer loads were slightly below the expected 90/10 weather conditions for 1994, 1999, 2001, and 2002, and weather conditions were slightly above the expected 90/10 weather during the 2006, 2011, and 2014 peaks. A spreadsheet containing historical annual peak loads and associated weather conditions since 1980 is available at http://www.iso-ne.com/markets/hstdata/rpts/ann_seasonal_pks/seasonal_peak_data_summary.xls.

Economy.com forecasts of New England gross state product (millions of 2005 $) from November 2012 and November 2013 forecasts.

Preliminary Forecast 2014–2023 presentation, slide 14 (http://www.iso-ne.com/static-assets/documents/committees/comm_wkgrps/prtcpnts_comm/pac/mtrls/2014/feb192014/a7_preliminary_iso_load_forecast_2014_2023.pdf).

2014 CELT Report (May 2014), http://www.iso-ne.com/static-assets/documents/trans/celt/report/2014/2014_celt_report_rev.pdf. Copies of all CELT reports are available at http://www.iso-ne.com/system-planning/system-plans-studies/celt. The ICR is the amount of capacity the New England region will need in a particular year to meet its NPCC resource adequacy planning criteria; see Section 4 for additional information. The ISO’s Forecast Data 2014 (April 30, 2014), worksheet 9 (http://www.iso-ne.com/static-assets/documents/trans/celt/fsct_detail/2014/isone_fcst_data_2014.xls) shows that the gross consumption of electric energy for 2023 is 151,525, gigawatt-hours (GWh). The savings attributable to federal appliance standards is 2,506 GWh for 2023. In addition, passive demand resources are projected to save 20,967 GWh for 2023 (see worksheet 2).

Other demand resources, an asset category that was retired on May 31, 2010, at the end of the transition period leading to the FCM, consisted of energy-efficiency measures, load management, and distributed generation—typically nondispatchable resources that tend to reduce end-use demand on the electricity network across many hours but usually not in direct response to changing hourly wholesale prices. For additional information on ODRs, refer to AMR10, Section 2.7, http://www.iso-ne.com/static-assets/documents/markets/mkt_anlys_rpts/annl_mkt_rpts/2010/amr10_final_060311.pdf.

Forecasts of net energy for load and peak loads are “gross loads.” Additional details of the loads are available using the “CELT Forecast Details” document-type filter at http://www.iso-ne.com/system-planning/system-plans-studies/celt. Also see the full 2014 CELT Report (http://www.iso-ne.com/static-assets/documents/trans/celt/report/2014/2014_celt_report_rev.pdf).

For additional information, refer to the ISO’s pricing node tables at http://www.iso-ne.com/stlmnts/stlmnt_mod_info/index.html.

State-sponsored EE programs consist of various efforts designed to reduce energy consumption. These efforts generally are funded by multiple sources, including a system benefits charge (SBC) applied to customer bills, the Regional Greenhouse Gas Initiative (RGGI) auction revenues (see Section 6.3.2.4), and state EE policy funds. More information on the methodology used to develop the EE forecast is available at the ISO’s “Energy-Efficiency Forecast Working Group,” webpage, http://www.iso-ne.com/committees/planning/energy-efficiency-forecast. ISO New England Energy-Efficiency Forecast Report for 2018 to 2023 (June 3, 2014), http://www.iso-ne.com/static-assets/documents/2014/08/eef_report_2018_2023_final.pdf.

Since its inception, the ISO has accounted for DG in its resource and load forecasts. Existing and future DG with obligations in the FCM are considered resources and contribute to meeting New England’s ICR. Existing non-FCM DG resources registered in the wholesale energy market are counted as “generating load assets” (i.e., settlement-only resources). Load reductions from the remainder of existing DG (i.e., installations that do not participate in the wholesale markets) are embedded in the historic loads used to develop the ISO’s 10-year load forecast.

- DG can use many technologies, including PV, wind, fuel cells, combined heat and power, and hydroelectric.

The DC nameplate rating of a PV installation is equal to the sum of the ratings of its solar panels, whereas its AC nameplate rating is determined by the sum of the rating(s) of its inverter(s).

Generically, the nameplate rating is a measure of a piece of equipment’s ability to produce or transmit electricity.

Of the DC electricity PV panels generate, 83% is converted into AC electricity, which is commonly used by utility customers.

State-jurisdictional standards are typically applicable for all solar projects, including both “rooftop” and MW-scale solar “farms.” New England presently does not include any FERC-jurisdictional PV project (~500 MW total); however, two projects currently in the ISO New England Generation Interconnection Queue (the queue) seeking interconnection may be FERC-jurisdictional and would need to meet the ISO’s small generator interconnection procedures (SGIP) or Small Generator Interconnection Agreement (SGIA) or both. See the OATT, Schedule 23, “Small Generator Interconnection Procedures” (July 25, 2012), http://www.iso-ne.com/static-assets/documents/regulatory/tariff/sect_2/sch23/sch_23_sgip.pdf.

The DGFWG is chaired by a representative of ISO New England and is not a formal NEPOOL committee or subcommittee. More information on the DGFWG, including the group’s scope of work (September 25, 2013) is available at http://www.iso-ne.com/static-assets/documents/committees/comm_wkgrps/othr/distributed_generation_frcst/2013mtrls/sep302013/draft_dgfwg_scope_of_work.pdf.

The DGFWG initial meeting provided an opportunity for the states to update the ISO on the breadth of their DG programs.

State PV policy data presented to the DGFWG is available at the ISO’s “Distributed Generation Forecast” webpage, http://www.iso-ne.com/system-planning/system-forecasting/distributed-generation-forecast. The ISO’s Generator Interconnection Queue includes the requests submitted by generators to interconnect to the ISO New England-administered transmission system; see Section 4.5.2.

Seasonal claimed capability is a generator's maximum production or output during a particular season, adjusted for physical and regulatory limitations.

A full explanation of the various discount factors and other modeling assumptions is contained in Discussion of PV Performance and ISO’s Draft Interim PV Forecast, DGFWG presentation (December 16, 2013), http://www.iso-ne.com/committees/comm_wkgrps/othr/distributed_generation_frcst/2013mtrls/dec162013/dg_forecast.pdf.

The policies differ for each state, and they have different end years. A discount of 25% was applied to the state goals for each of the policy years shown in the table. The megawatt growth beyond the last known policy year is considered constant, but a discount factor of 75% was applied rather than the 25%,

Various planning studies may use values that differ from the SSCC, depending on the study assumptions and intent.

The annual PV energy output calculation assumes an estimated 15.4% capacity factor on the basis of AC nameplate capacity.

The ISO will coordinate the use of the DG forecast with the PAC and the appropriate NEPOOL technical committees.

See Update on DG Location and Modeling Issues, DGFWG presentation (April 2, 2014), http://www.iso-ne.com/committees/comm_wkgrps/othr/distributed_generation_frcst/2014mtrls/apr22014/dg_location_modeling.pdf.

Deterministic analyses are snapshots of assumed specific conditions that do not quantify the likelihood that these conditions will actually materialize. The results are based on analyzing the assumed set of conditions representing a specific scenario.

Established ICR values refer to the values that either FERC has approved or the ISO has filed with FERC for approval. Representative net ICR values are the representative ICRs for the region, minus the tie-reliability benefits associated with the Hydro-Québec Interconnection Capability Credits (HQICCs). As defined in the ISO’s tariff, the HQICC is a monthly value that reflects the annual installed capacity benefits of the HQ Interconnection, as determined by the ISO using a standard methodology on file with FERC. The ISO calculates representative net ICR values solely to inform New England stakeholders; these values have not and will not be filed with FERC for approval. The values for FCA #9 for the 2018/2019 CCP are scheduled to be filed with FERC in November 2014. For additional information about ICRs, see the ISO’s “Installed Capacity Requirements,” webpage at http://www.iso-ne.com/system-planning/resource-planning/installed-capacity-requirements.

ISO New England, 2013–2022 Forecast Report of Capacity, Energy, Loads, and Transmission (May 2013), http://www.iso-ne.com/static-assets/documents/trans/celt/report/2013/2013_celt_report.pdf.

The footnote above defines the HQICC monthly value used to modify the ICR.

Resulting reserves are the amount of capacity in excess of the forecast 50/50 peak load. Percentage resulting reserves = [{(Net ICR − 50/50 peak load) ÷ 50/50 peak load} × 100]. Based on the CELT 2013 forecast, the average value of the resulting reserves for 2015/2016 through 2017/2018 is 14.2%, derived from the following values: 14.9% for 2015/2016, 14.2% for 2016/2017, and 13.6% for 2017/2018.

LSRs and MCLs are based on network models using transmission facilities that will be in service no later than the first day of the relevant capacity commitment period.

The ICR requirements for 2013/2014 to 2017/2018 are available in the FERC filings at
http://www.iso-ne.com/regulatory/ferc/filings/2011/mar/er11-3048-000_03-08-11_icr_2014-2015.pdf,
http://www.iso-ne.com/regulatory/ferc/filings/2012/jan/er12-756-000_01-03-12_icr_2015-2016_filing.pdf,
http://www.iso-ne.com/regulatory/ferc/filings/2012/nov/er13-495-000_11-30-12_icr_aras.pdf, and http://www.iso-ne.com/regulatory/ferc/filings/2013/feb/er13-992-000_2-26-13_7th_fca_results_filing.pdf. The ISO filed with FERC the results of FCA #8, which was held on February 3, 2014, for the 2017/2018 capacity commitment period. ISO New England Inc., Forward Capacity Auction Results Filing, http://www.iso-ne.com/regulatory/ferc/filings/2014/feb/er14_1409-000_fca8_results_filing_2-28-2014.pdf. The ISO provided the PAC with representative values for LSRs for both NEMA/Boston and Connecticut and an MCL for Maine. See Future Representative Capacity Requirements for 2018/19–2022/23, PAC presentation (December 18, 2013), http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/mtrls/2013/dec182013/a5_representative_icr_values_pac_121813.pdf.

A capacity supply obligation is a requirement for a resource to provide capacity, or a portion of capacity, to satisfy a portion of the ISO’s Installed Capacity Requirement acquired through a Forward Capacity Auction, a reconfiguration auction, or a CSO bilateral contract through which a market participant may transfer all or part of its CSO to another entity. FCM reconfiguration auctions take place before and during the capacity commitment period to allow participants to buy and sell capacity obligations and adjust their positions.

The 2014 CELT Report, Section 3 and Appendix D (May 2014) (http://www.iso-ne.com/static-assets/documents/trans/celt/report/2014/2014_celt_report_rev.pdf) contains the FCM capacity supply obligations for all capacity resources by load zone.

FERC, Order on Tariff Revisions to the Forward Capacity Market (March 30, 2012), http://www.iso-ne.com/regulatory/ferc/orders/2012/mar/er12-953-000_3-30-12_order_fcm_redesign_ext.pdf.

ISO New England, Compliance Filing Revisions to Forward Capacity Market Rules (December 3, 2012), http://www.iso-ne.com/regulatory/ferc/filings/2012/dec/er12-953-001_12-3-12_fcm_redesign_compl.pdf.

FERC, Order Accepting in Part, and Rejecting in Part, FCM Compliance Filing (February 12, 2013), http://www.iso-ne.com/regulatory/ferc/orders/2013/feb/er12-953-001_2-12-13_order_fcm_compliance.pdf; FERC, Order on Compliance Filing (May 31, 2013), http://www.iso-ne.com/regulatory/ferc/orders/2013/may/er12-953-002_5-31-13_order_accept_fcm_compliance.pdf.

Most of this increase is attributable to the certification of the Interstate Reliability Project (IRP) (see Section 5.4.2), which results in the Lake Road Station being considered inside the CT import interface, starting with the 2017/2018 capacity commitment period.

An administrative export delist bid is a type of bid submitted during a Forward Capacity Auction for a capacity export resource associated with multiyear contracts but wanting to opt out of a capacity supply obligation.

A nonprice retirement request is an irrevocable request submitted in a Forward Capacity Auction to retire the entire capacity of a resource, subject to an ISO review for reliability impacts and that supersedes any delist bids submitted. If the ISO determines the resource is needed for reliability, the resource owner can either retire the resource as requested or continue to operate it until the reliability need has been met and then retire the resource.

ISO New England, “Nonprice Retirement Requests and Determinations,” webpage (2014), http://www.iso-ne.com/genrtion_resrcs/reports/sts_non_retrmnt_rqst/index.html.

Market Rule 1, Section III.13.2.8.2, details the conditions that determine insufficient competition.

ISO New England, Compliance Filing of ISO New England Inc., FERC filing (January 31, 2014), http://www.iso-ne.com/regulatory/ferc/filings/2014/jan/er12-953-004_1-31-2014_comp_12-953-002.pdf. FERC, Order Accepting Compliance Filing, FERC order (April 28, 2014), http://www.iso-ne.com/regulatory/ferc/orders/2014/apr/er12-953-004-4-28-14_order_accept_cap_zone_compliance.pdf.

Forward Capacity Market: 2014 Network Topology Certifications, Reliability Committee presentation (January 21, 2014), http://www.iso-ne.com/committees/comm_wkgrps/relblty_comm/relblty/mtrls/2014/jan212014/index.html, A6 FCA #9 Transmission Certification Update, zip file.

ISO New England, “FCM 2014 Network Topology Certifications,” memo to the NEPOOL Reliability Committee (February 13, 2014), http://www.iso-ne.com/committees/comm_wkgrps/relblty_comm/relblty/mtrls/2014/feb182014/a_rc_memo_2014_fcm_irp_certification.pdf.

2017-2018 Capacity Commitment Period—Evaluation of Nonprice Retirements, RC presentation (October 15, 2013), http://www.iso-ne.com/static-assets/documents/committees/comm_wkgrps/relblty_comm/relblty/mtrls/2013/oct152013/a5_npr_summary.pptx.

Transmission Interface Transfer Capabilities: 2014 Regional System Plan Assumptions, PAC presentation (January 23, 2014), http://www.iso-ne.com/static-assets/documents/2014/09/a7_rsp14_transmission_interface_transfer_capabilities_assumptions.pdf.

Transmission Interface Transfer Capabilities: 2014 Regional System Plan Assumptions—Part 2, PAC presentation (February 20, 2014), http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/mtrls/2014/feb202014/a3_rsp_2014_transfer_capability_assumptions_2.pdf.

Transmission Interface Transfer Capabilities: 2014 Regional System Plan Assumptions—Part 3, PAC presentation (March 17, 2014), http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/mtrls/2014/mar172014/a8_rsp14_transmission_interface_transfer_capabilities.pdf.

Transmission Interface Transfer Capabilities: 2014 Regional System Plan Assumptions—Part 4, PAC presentation (March 24, 2014), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2014/mar242014/a6_rsp14_transfer_capability_assumptions_pt4.pdf.

See the May 31, 2013, FERC order (http://www.iso-ne.com/regulatory/ferc/orders/2013/may/er12-953-002_5-31-13_order_accept_fcm_compliance.pdf).

ISO Operating Procedure No. 8, Operating Reserve and Regulation (May 2, 2014), http://www.iso-ne.com/rules_proceds/operating/isone/op8/op8_rto_final.pdf.

ISO Operating Procedure No. 19, Transmission Operations (September 2, 2012), http://www.iso-ne.com/rules_proceds/operating/isone/op19/op19_rto_final.pdf.

Also see New England Regional System Plan (RSP13) Representative Future Locational Forward Reserve Requirements, PAC presentation (June 19, 2013), http://www.iso-ne.com/static-assets/documents/committees/comm_wkgrps/prtcpnts_comm/pac/mtrls/2013/jun192013/a8_representative_operating_reserve_requirements.pdf.

While the estimates for operating-reserve requirements are based on expected future operating conditions, annual market requirements are based on historical data that reflect the actual previous seasonal system conditions, as adjusted for transmission topology changes and resource retirements and additions. ISO market requirements are calculated immediately before each locational FRM procurement period.

Market Rule 1, Standard Market Design (ISO tariff, Section III) (2014), defines the types of reserves that can meet these requirements; http://www.iso-ne.com/regulatory/tariff/sect_3/index.html.

Economic-merit order (i.e., in merit or in merit order) is when the generators with the lowest-price offers are committed and dispatched first, and increasingly higher-priced generators are brought on line as demand increases. Out-of-merit dispatch occurs when generators are run less economically to respect system reliability requirements.

Although physically in Connecticut, the Lake Road generating plant is considered electrically part of Rhode Island without the completion of the NEEWS Interstate Reliability Project.

In some circumstances, when transmission contingencies are more severe than generation contingencies, shedding some load may be acceptable.

Operating Procedure No. 4, Action during a Capacity Deficiency (October 5, 2013), and Operating Procedure No. 7, Action in an Emergency (June 26, 2013), http://www.iso-ne.com/participate/rules-procedures/operating-procedures.

RSP14 Resource Adequacy and Related Studies, PAC presentation (April 29, 2014), http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/mtrls/2014/apr292014/a5_rsp14_resource_adequacy_and_related_studies.pdf.

The ISO provides monthly updates on the status of active generation interconnection requests, NEPOOL Participant Committee COO Report for Monthly Updates (Monthly COO Report). See the April 2014 monthly COO Report in the NEPOOL Participant Committee materials at http://www.iso-ne.com/static-assets/documents/committees/comm_wkgrps/prtcpnts_comm/prtcpnts/mtrls/2014/apr42014/coo_report_apr_2014.pdf.

The CMA subarea in Massachusetts and SME subarea in Maine have no megawatts proposed in the active queue.

In addition to the Monthly COO Reports, information on the queue is available at http://www.iso-ne.com/system-planning/transmission-planning/interconnection-request-queue.

The projects proposed but discontinued faced problems associated with financing, licensing, insufficient market incentives, or other issues.

Higher tie-reliability benefits and reductions in the net ICR would increase the frequency and depth of OP 4 actions.

Past RSPs are available at http://www.iso-ne.com/trans/rsp/index.html. PAC materials and reports are available at http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/index.html.

ISO New England, Transmission Planning Process Guide, draft, http://www.iso-ne.com/static-assets/documents/committees/comm_wkgrps/prtcpnts_comm/pac/plan_guides/plan_process_guide/planning_process_guide_for_february_pac_2_5_2013__3_.docx. Transmission Planning Technical Guide, draft, http://www.iso-ne.com/static-assets/documents/committees/comm_wkgrps/prtcpnts_comm/pac/plan_guides/plan_tech_guide/planning_technical_guide_clean_12_06_2013.pdf.

See the OATT, Section II.B, Attachment N, “Procedures for Regional System Plan Upgrades,”
http://www.iso-ne.com/static-assets/documents/regulatory/tariff/sect_2/oatt/sect_ii.pdf.

The Network Capability Interconnection Standard is an energy-only standard that includes the minimum criteria required to permit a generator to connect to the transmission system so that it has no adverse impacts on the reliability, stability, or operation of the system, including the degradation of transfer capability for interfaces affected by the generating facility. The Capacity Capability Interconnection Standard is a capacity and energy standard that includes the same criteria as the Network Capability Interconnection Standard but also includes criteria to ensure intrazonal deliverability by avoiding the redispatch of other capacity network resources. Before October 29, 1998, Generator Interconnection-Related Upgrades included cost responsibility for additional upgrades beyond those required to satisfy the minimum interconnection standard. The OATT, Section 22, defines the standards; http://www.iso-ne.com/static-assets/documents/regulatory/tariff/sect_2/sch22/sch_22_lgip.pdf.

The filing for the addition or modification to the transmission upgrade must be in accordance with the OATT, Section II.47.2, on a date after the RSP Project List (as of the date of that application) already has documented the addition or modification, other than as an Elective Transmission Upgrade.

Elective Transmission Upgrade Process Improvements Background and Project Scope, Joint Reliability Committee and Transmission Committee Summer Meeting Presentation (August 11–12, 2014), http://www.iso-ne.com/static-assets/documents/committees/comm_wkgrps/trans_comm/tariff_comm/mtrls/2014/aug11122014/a3_etu_presentation_summer_meeting.pptx.

Pool transmission facilities are the facilities rated 69 kV or above owned by the participating transmission owners, over which the ISO has operating authority in accordance with the terms set forth in the Transmission Operating Agreements. Refer to the OATT, Section II.49, 109, for additional specifications, http://www.iso-ne.com/static-assets/documents/regulatory/tariff/sect_2/oatt/sect_ii.pdf.

PAC materials and meeting minutes are available at http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/index.html. The RSP Project List (XLS file) is available at http://www.iso-ne.com/system-planning/system-plans-studies/rsp.

The range for the $4.5 billion cost estimate is $3.7 to $5.3 billion.

Regional transmission service is comprised of regional network service (RNS) and through or out (TOUT) service. RNS is the transmission service the ISO provides over the PTFs, described in the OATT, Part II.B, that network customers use to serve load within the New England Control Area. The ISO’s TOUT service over the PTFs allows a real-time market transaction to be exported out of or “wheeled through” the New England area, including services used for network resources or regional network load not physically interconnected with a PTF. The PTO Administrative Committee is expected to make a supplemental filing on or before February 28, 2015, that will update New England Power Company’s transmission revenue requirement, which will revise the 2014 regional transmission service rates. See FERC, letter order to National Grid, Docket No. ER14-1686-000 (June 6, 2014), http://www.ferc.gov/CalendarFiles/20140606132455-ER14-1686-000.pdf.

One exception is that Aroostook and Washington Counties in Maine are served radially from New Brunswick.

Section 242 Rebuild, PAC presentation (September 17, 2013), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2013/sep172013/a5_section_242_line_rebuild.ppt.

National Grid Transmission Facility Refurbishments, Update to Salem Harbor Cable Replacement Solution, PAC presentation (November 20, 2013), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2013/nov202013/a7_asset_condition_needs_salem_harbor_cable_replacement.pdf.

Asset Condition Needs: 115 kV Salem Harbor Substation, PAC presentation (November 20, 2013), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2013/nov202013/a8_salem_harbor_substation.pdf.

Old Town 115/13.8 kV Substation Solutions Study, PAC presentation (June 19, 2014), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2014/jun192014/a9_old_town_solution_study.pdf.

Sandy Pond Substation Refurbishment—Ayer, MA, Needs and Preferred Solution, PAC presentation (February 19, 2014), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2014/feb192014/a10_sandy_pond_substation_conditions.pdf.

Housatonic River Crossing Needs Assessment and Solutions Study, PAC presentation (March 17, 2014), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2014/mar172014/a6_housatonic_river_crossing_needs_assment_solution_study.pdf.

National Grid’s New England Transmission Line Asset-Condition Refurbishment Program and Projects, PAC presentation (March 24, 2014), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2014/mar242014/a3_ngrid_transmission_lines_asset_conditions_refurbishment_and_projects.pdf.

PV20 Cable Replacement, PAC presentation (June 5, 2014), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2014/jun192014/a10_pv20_cable_replacement.pdf.

Baird 115/13.8 kV Substation Solutions Study, PAC presentation (June 19, 2014), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2014/jun192014/a8_baird_substation_study.pdf.

Further details about individual transmission projects can be obtained by contacting ISO Customer Service at (413) 540-4220.

The flows vary with system conditions, as shown by the 2012 historical market data, which include the occurrence of northbound flows. See RSP14 20132012 Historical Market Data: Locational Marginal Prices, Interface MW Flows, PAC presentation (February 19, 2014), http://www.iso-ne.com/static-assets/documents/committees/comm_wkgrps/prtcpnts_comm/pac/mtrls/2014/feb192014/a6_2014_lmp_interface_flows.pdf.

Wind Development in Constrained Areas, PAC presentation (March 21, 2013), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2013/mar212013/a5_wind_development_in_constrained_areas_new.pdf.

Maine Power Reliability Program Steady State Needs Assessment, PAC presentation (May 14, 2007), https://smd.iso-ne.com/trans/sys_studies/rsp_docs/pres/2007/maine_power_reliability_program_steady_state_needs_assessment.pdf. Final Report Maine Power Reliability Program Needs Assessment of the Maine Transmission System (June 19, 2007), https://smd.iso-ne.com/trans/sys_studies/rsp_docs/pres/2007/maine_power_reliability_program_needs_assessment_final_report.pdf.

Northern Maine System Performance, PAC presentation (September 21, 2010), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2010/sep212010/northern_maine.pdf.

Maine Power Reliability Program: Transfer Capability Study Results, PAC presentation (December 13, 2012), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2012/dec132012/mprp_transfer_limits.pdf.

Wind Development in Constrained Areas, PAC presentation (March 21, 2013), see link above.

The Vermont Long-Range Transmission Plan identifies reliability concerns and the transmission alternatives to address these concerns. The plan serves as the basis for considering whether alternatives, including new generation and energy efficiency, can meet Vermont's reliability needs. It also provides information about transmission projects that may be needed to maintain grid reliability.

VELCO, 2012 Vermont Transmission System Long-Range Plan (July 1, 2012), http://www.velco.com/LongRange/Pages/2012Long-RangeTransmissionPlan.aspx.

New Hampshire/Vermont Transmission System 2011 Needs Assessment (November 2011), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/reports/2011/nhvt_2011_needs.pdf.

Nontransmission Alternatives Analysis, Results of the NH/VT Pilot Study (May 26, 2011), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2011/apr132011/nta.pdf.

NYISO and NYPA have informed ISO New England that in February 2014 the Moses-Willis 230 kV double-circuit towers (DCTs) in northern New York were separated. Interregional planning studies are coordinated through the Joint ISO/RTO Planning Committee (JIPC) (see Section 7.1).

Follow-Up Analysis to the New Hampshire/Vermont Solutions Study (NH/VT Solutions Study Follow Up) (April 2012), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/reports/2012/final_nhvt_solutions_followup.pdf. Final NH/VT Transmission Follow-Up Appendices (April 13, 2012), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/reports/2012/nhvt_sol_followup_apps.pdf. Also see the ISO’s webpage, “New Hampshire and Vermont Key Study Area,” http://www.iso-ne.com/system-planning/key-study-areas/vt-nh.

New Hampshire/Vermont Transmission Solutions Study Report (April 2012), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/reports/2012/nhvt_solutions_report.pdf.

New Hampshire/Vermont 2022 Needs Assessment Study Scope (June 2013), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/reports/2013/a_final_nh_vt_2022_needs_scope.pdf.

New Hampshire/Vermont 2023 Needs Assessment Update (March 2014), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2014/mar172014/a7_nh_vt_2023_needs_assessment.pdf.

New Hampshire/Vermont 2022 Needs Assessment Results (June 2013), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2013/jun192013/a2_nh_vt_2022_needs_assessment.zip.

Overview—New Hampshire Second Deerfield Autotransformer, PAC presentation (June 4, 2008), https://smd.iso-ne.com/trans/sys_studies/rsp_docs/pres/2008/deerfield_area.pdf. New Hampshire Second Deerfield Autotransformer—Update to June 2008, PAC presentation (December 16, 2008), https://smd.iso-ne.com/trans/sys_studies/rsp_docs/pres/2008/deerfield.pdf. Second 345/115-kV Deerfield Autotransformer Proposed Plan Application Analysis, final report (May 2009), zip file, http://www.iso-ne.com/search?query=New%20Hampshire%20Second%20Deerfield%20Autotransformer.

Bangor Hydro Electric Co., Chester Static VAR Compensator Control Replacement, PAC presentation (January 18, 2012), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2012/jan182012/chester_svc.pdf.

MPRP Steady State Needs Assessment, PAC presentation (May 14, 2007), https://smd.iso-ne.com/trans/sys_studies/rsp_docs/pres/2007/maine_power_reliability_program_steady_state_needs_assessment.pdf. MPRP Needs Assessment of the Maine Transmission System, final report (June 19, 2007), https://smd.iso-ne.com/trans/sys_studies/rsp_docs/pres/2007/maine_power_reliability_program_needs_assessment_final_report.pdf.

Maine Power Reliability Program Transmission Alternatives—Revised, PAC presentation (January 24, 2008), https://smd.iso-ne.com/trans/sys_studies/rsp_docs/pres/2008/amprprevised.pdf. Final Report Maine Power Reliability Program Transmission Alternatives Assessment for the Maine Transmission System (June 10, 2008), https://smd.iso-ne.com/trans/sys_studies/rsp_docs/pres/2008/mprp_final_report.pdf. The Maine Power Reliability Program Transmission Alternatives Assessment for the Maine Transmission System (May 30, 2008) describes the original version of this project in more detail. The CMP Maine Power Reliability Program Proposed Plan Application Analyses Addendum Report (February 6, 2009) updates the project descriptions.

Because the Maine Public Utilities Commission (MPUC) approved the “Lewiston Loop” section of the MPRP subsequent to approving most of the MPRP, this part of the project currently has an in-service date of early 2017.

The 345 kV Reliability Project in Boston added new 345 kV cables between Stoughton, Hyde Park, and K Street substations and is often referred to as the Stoughton Cables Project. In Southwest Connecticut, the Phase I Project added a new 345 kV circuit between Plumtree and Norwalk substations and often is referred to as the Bethel–Norwalk Project. The Phase II project added a new 345 kV circuit between Beseck, East Devon, Singer, and Norwalk substations and is often referred to as the Middletown–Norwalk Project.

A lower load forecast, new supply and demand resources, and the potential unavailability of the Vermont Yankee generating facility drove the need to reassess these upgrades. An area with constantly growing load and no added new resources would not need reassessment.

Greater Hartford and Central Connecticut Area Transmission 2022 Needs Assessment (May 2014), zip file, http://www.iso-ne.com/search?query=Greater%20Hartford%20and%20Central%20Connecticut%20Area%20Transmission%202022%20Needs%20Assessment.

New England East–West Solution Rhode Island and Springfield Current Needs Assessments (June 17, 2009), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2009/jun172009/neews.pdf.

NEEWS: Interstate Reliability Project Component Updated Needs Assessment (April 2011), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/reports/2011/neews_interstate_final.pdf.

NEEWS: Interstate Reliability Project Component Updated Solutions Study Report (February 2012), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/reports/2012/neews_interstate_solution.pdf.

Follow-Up Analysis to the 2011 NEEWS: Interstate Reliability Project Component Updated Needs Assessment (September 2012), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/reports/2012/neews_needs_addendum_final.pdf.

Follow-Up Analysis to the 2012 NEEWS: Interstate Reliability Project Component Updated Solution Study (September 2012), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/reports/2012/neews_sol_addendum_final.pdf.

The original Interstate Project included the following major components: a new Millbury–West Farnum–Lake Road–Card Street 345 kV line and associated substation upgrades; four 345 kV, 120 MVAR capacitor banks at Montville; and the looping in of the Millstone–Manchester 345 kV line into the Card Street substation.

Brayton Point Station Nonprice Retirement (February 18, 2014), https://smd.iso-ne.com/committees/comm_wkgrps/relblty_comm/relblty/ceii/ceii_mtrls/2014/feb182014/a8_brayton_py_npr_follow_up_analysis.pdf.

Greater Boston Area Transmission Needs Assessment (July 2010) can be accessed at http://www.iso-ne.com/system-planning/key-study-areas/greater-boston.

The ISO had previously identified a preferred AC solution from several considered alternatives for the area. At the request of stakeholders, the ISO began evaluating another alternative that was offered after the close of the original alternative review and after a preferred solution was identified. ISO New England, “Greater Boston Key Study Area,” webpage (2014), http://www.iso-ne.com/system-planning/key-study-areas/greater-boston.

Evaluation of Need for Footprint Combined Cycle for the 2016/2017 and 2017/2018 Capacity Commitment Periods Summary Report (August 2014), https://smd.iso-ne.com/committees/comm_wkgrps/relblty_comm/relblty/ceii/ceii_mtrls/2014/aug152014/a4_footprint_power_evaluation_of_need_report.pdf.

Advanced Greater Boston Solutions—Update, PAC presentation (June 19, 2014), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2014/jun192014/a7_greater_boston_north_cambridge_stuck_breaker.pdf.

NSTAR Underground Cable Ratings Update, PAC presentation (April 2013), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2013/apr242013/a10_nstar_greater_boston_cable_ratings.pdf.

Greater Boston Study Needs Assessment/Solution Study Status Update, PAC presentation (March 2012), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2012/mar142012/gbwg_update.pdf.

Greater Boston Solutions Study Update, PAC presentation (June 19, 2014), http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/mtrls/2014/jun192014/a4_greater_boston_solution_study_cost_estimates.pdf.

Pittsfield–Greenfield, MA, Area Transmission: Preferred Solution and Alternatives Study, PAC presentation (October 2010), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2010/oct212010/pittsfield_greenfield.pdf.

Pittsfield–Greenfield 2022 Needs Assessment: N-1 and N-1-1 Results, PAC presentation (July 9, 2013), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2013/jul92013/a4_pittsfield_greenfield_needs_assessment_rev1.pdf.

SWCT Area Transmission Needs Assessment (July 13, 2011), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/reports/2011/final_swct_needs_report.pdf.

SWCT Update on Continuing Alternatives Analyses (November 16, 2011), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2011/nov162011/swct_solution_study.pdf.

Southwest Connecticut Advanced Solutions Introduction (April 13, 2011), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2011/apr132011/swct_adv_sol_intro.pdf.

SWCT Advanced Solutions Mill River to Quinnipiac 8300 Line Reconfiguration Project (April 13, 2011), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2011/apr132011/8300_line.pdf.

SWCT Advanced Solutions Stamford Reliability Project (April 13, 2011), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2011/apr132011/stamford.pdf.

Southwest Connecticut 2022 Needs Assessment (May 23, 2013), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2013/may232013/a3_swct_needs_assessment_052313.pdf.

Southwest Connecticut 2022 Needs Assessment II (February 19, 2014), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2014/feb192014/a9_swct_needs_assessment_2.pdf. Southwest Connecticut Area Transmission 2022 Needs Assessment (June 2014), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/reports/2014/final_swct_2022_needs.pdf.

Greater Hartford and Central Connecticut Working Group (ISO New England, Northeast Utilities, and United Illuminating), Greater Hartford and Central Connecticut Area Transmission 2022 Needs Assessment (April 2014), http://www.iso-ne.com/system-planning/key-study-areas/greater-hartford.

Eastern Connecticut Area Needs Assessment Updates, PAC presentation (July 9, 2013), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2013/jul92013/a3_eastern_ct_final_needs_assessment.pdf.

The PTOs have certified that the IRP project would be in service by December 2015 and have listed this as the project’s in-service date in the RSP Project List. The ISO has accepted the PTO’s certification of the IRP project for FCA #8, and has accepted—for conducting the calculations described in Section 4—that the project will be in service by June 1, 2017, although it may be in service before that date.

Western Massachusetts Transmission Reinforcements 2007 to 2017 (September 2007), http://www.iso-ne.com/committees/comm_wkgrps/relblty_comm/relblty/mtrls/2007/oct102007/zip2_western_ma_ppa.zip.

National Grid, Auburn St. Substation Upgrades System Impact Study (November 2007) and Auburn St. Substation and Area Transmission System Reliability Study (July 2007), http://www.iso-ne.com/committees/comm_wkgrps/relblty_comm/relblty/mtrls/2007/dec192007/Zip%203%20auburn%20area.zip.

Lower SEMA Short-Term Upgrades System Impact Study Steady-State Analysis (May 3, 2007), http://www.iso-ne.com/committees/comm_wkgrps/relblty_comm/relblty/mtrls/2007/aug82007/zip1b_study-reports.zip.

This circuit’s designated line number is “115,” coincidentally the same as the voltage class.

Greater Rhode Island Transmission Reinforcements (March 2008), http://www.iso-ne.com/committees/comm_wkgrps/relblty_comm/relblty/mtrls/2008/apr152008/zip1_gri-study-reports.zip.

SWCT Advanced Solutions–Mill River to Quinnipiac 8300 Line Reconfiguration (April 13, 2011), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2011/apr132011/8300_line.pdf.

SWCT Advanced Solutions–Stamford Reliability Project (April 13, 2011), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2011/apr132011/stamford.pdf.

Advanced Greater Boston Solutions, (December 2013), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2013/dec182013/a6_nu_advanced_greater_boston_solutions.ppt.

Advanced Greater Boston Solutions, see above note.

Advanced Greater Boston Solutions—West Walpole to Holbrook N-1-1 Loss of Load, Needs and Preferred Solution (February 2014), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2014/feb192014/a4_advanced_greater_boston_west_walpole_to_holbrook_needs_and_solutions.pdf.

Advanced Greater Boston Solutions—Update, PAC presentation (June 19, 2014), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2014/jun192014/a7_greater_boston_north_cambridge_stuck_breaker.pdf.

Follow-Up Analysis to the New Hampshire/Vermont Solutions Study (April 2012), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/reports/2012/final_nhvt_solutions_followup.pdf.

Greater Boston Needs Assessment/Solutions Study Status Update, PAC presentation (June 28, 2011), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2011/jun302011/greater_boston.pdf. Greater Hartford and Central Connecticut Area Needs Assessment II, PAC presentation (January 16, 2013), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2013/jan162013/a8_ghcc_needs_assessment_ii_011613.pdf.

NCPC is a “make-whole” payment to a supply resource that responded to the ISO’s dispatch instructions but did not fully recover its start-up and operating costs in either the Day-Ahead Energy Market or Real-Time Energy Market.

ISO New England, Forward Capacity Auction Results, FERC filing (August 30, 2010), http://www.iso-ne.com/regulatory/ferc/filings/2010/aug/er10-2477-000_08-30-10_fca_4_results.pdf. FERC, Order on Forward Capacity Auction Results Filing (December 16, 2010), http://www.iso-ne.com/regulatory/ferc/orders/2010/dec/er10-2744-000_12-16-10_order_fca_results.pdf.

A nonprice retirement request is an irrevocable request submitted in a FCA to retire the entire capacity of a resource, subject to an ISO review for reliability impacts and that supersedes any other delist bids submitted. If the ISO determines the system needs the resource for reliability, the resource owner can either retire the resource as requested or continue to operate it until the reliability need has been met and then retire the resource. Nonprice retirement requests, determination letters, and resource responses in 2011 are available at http://www.iso-ne.com/system-planning/resource-planning/nonprice-retirement.

ISO New England, Forward Capacity Auction Results, FERC filing (June 27, 2011), http://www.iso-ne.com/regulatory/ferc/filings/2011/jun/er11-3891-000_06-27-11_fca_5_results_filing.pdf.

ISO New England, Forward Capacity Auction Results, FERC filing (April 30, 2012), XLSX file, http://www.iso-ne.com/isoexpress/web/reports/auctions/-/tree/fcm-auction-results.

An administrative export delist bid for 100 MW also was submitted for FCA #7, but the ISO does not review or analyze this type of bid. Thus, the total for all delist bids for this FCA was 1,660 MW. Refer to the ISO’s Markets Overview Report for more information on delist bids (http://www.iso-ne.com/pubs/spcl_rpts/2014/2014_market_overview_050614.pdf).

RSP14 2013 Historical Market Data: Locational Marginal Prices Interface MW Flows, PAC presentation, slide 7 (February 19, 2014), http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/mtrls/2014/feb192014/a6_2014_lmp_interface_flows.pdf.

This total includes seven projects in 2002, 26 projects in 2003, 30 projects in 2004, 51 projects in 2005, 55 projects in 2006, 36 projects in 2007, 64 projects in 2008, 38 projects in 2009, 37 projects in 2010, 44 projects in 2011, 60 projects in 2012, 90 projects in 2013, and 21 additional projects through June 2014. The June 2014 RSP Project List shows that 44 more projects are due in service by the end of 2014.

ISO New England, “Strategic Planning Initiative,” webpage (2014), http://www.iso-ne.com/committees/comm_wkgrps/strategic_planning_discussion/index.html.

Approximately 2,035 MW of fossil-fired steam generating capacity at Bridgeport Harbor, Norwalk Harbor, and Brayton Point stations and the 619 MW Vermont Yankee nuclear unit will be retired (through nonprice retirements) by June 1, 2017.

Energy Information Administration (EIA), “Natural Gas Consumption by End Use,” webpage (US Department of Energy [DOE], July 31, 2013), http://www.eia.gov/dnav/ng/ng_cons_sum_dcu_nus_m.htm.

FERC and the North American Energy Standards Board (NAESB) have held several forums to discuss the lack of alignment between the natural gas and wholesale electricity market trading days. See the Gas-Electric Harmonization Forum Survey at http://www.naesb.org/committee_activities.asp. Also, FERC has issued a notice of proposed rulemaking (NOPR), Coordination of the Scheduling Processes of Interstate Natural Gas Pipelines and Public Utilities, 146 FERC ¶ 61,201, 18 CFR Part 284 (March 20, 2014), http://www.ferc.gov/industries/electric/indus-act/electric-coord.asp.

GDF SUEZ Gas NA, the owner of the Neptune LNG Deepwater Port, requested and received from the US Maritime Administration (of the US Department of Transportation) the suspension of its license to operate this port. Under the terms of the suspension, however, GDF SUEZ Gas NA has the right to pursue the reinstatement of this license and the resumption of port operations.

EIA, “US Liquefied Natural Gas Imports,” webpage table (DOE, July 31, 2013), http://www.eia.gov/dnav/ng/hist/n9103us2m.htm.

DOE/EIA, Annual Energy Outlook 2014 (AEO 2014), Table 132, “Lower 48 Natural Gas Production and Supply Prices by Supply Region—Reference Case.” The statistics are for dry gas production, which is natural gas that has been processed to remove heavier hydrocarbons (i.e., natural gas liquids—pentane, butane, ethane, and others). Marcellus Shale gas is a recently developed source of natural gas located in central Pennsylvania.

One dekatherm (Dth) is approximately equivalent to one million British thermal units (MMBtu) and 1,000 cubic feet (Mcf).

Sital Mody, Embracing Change—Tennessee Gas Pipeline, slides 8 and 9, presentation at the Northeast Gas Association, Regional Market Trends Forum, Hartford, CT (Kinder Morgan, May 1, 2014), http://www.northeastgas.org/pdf/s_mody.pdf. These slides showed the Northeast Expansion Project in active development mode, with projected volumes of 0.8 to 2.2 billion cubic feet per day (Bcf/d) based on shipper interests.

EIA, Short-Term Energy Outlook (February 11, 2014). US average heating-degree days (i.e., an indication of colder weather) were 12% higher than last winter and 8% above the previous 10-year average. The Northeast was 11% colder than last winter; the Midwest, 17% colder; and the South, 20% colder, while the West was 3% warmer. New England was approximately 7.5% colder than normal.

Nine days in January 2014 were in the coldest 5% of all winter days over the past 20 years.

Oil prices exceeded natural gas prices 43% of the time; natural gas had an average price of $19.33/MMBtu.

FERC, ISO New England Inc., et al. Order Conditionally Accepting Tariff Revisions (September 16, 2013), http://www.iso-ne.com/regulatory/ferc/orders/2013/sep/er13-1851-000_9-16-2013_winter_rel.pdf.

No. 6 oil is the crude-oil component remaining after gasoline and distillate fuel oils have been extracted and is used by oil-burning power plants. No. 6 oil (1%) refers to the percentage of sulfur in the oil and is referred to as a residual fuel oil or heavy fuel oil.

ISO New England Inc., Docket No. ER14-___-000, Winter 2014-15 Reliability Program (Parts 1 and 2), FERC filing (July 11, 2014), http://www.iso-ne.com/static-assets/documents/regulatory/ferc/filings/2014/jul/er14_2407_000_win_rel_pro_7_11_2014.pdf and http://www.iso-ne.com/regulatory/ferc/filings/2014/jul/er14-2407-001_winter_rel_7-11-2014.pdf. The summer seasonal claimed capability of Vermont Yankee is 619 MW. The nonprice retirement of VY is based on its capacity supply obligation of 604 MW.

Electric energy offers more reflective of actual fuel prices and thus the cost of procuring fuel in real time will improve energy market price signals. The revisions to offer-flexibility rules are targeted to be implemented by the end of 2014. ISO New England Inc. and NEPOOL, Energy Market Offer Flexibility Changes, FERC filing, (July 1, 2013), http://www.iso-ne.com/static-assets/documents/regulatory/ferc/filings/2013/jul/er13_1877_000_mkt_offer_flex_7_1_2013.pdf. FERC, Order Conditionally Accepting Tariff Revisions (October 3, 2013), http://www.iso-ne.com/regulatory/ferc/orders/2013/oct/er13-1877-000_10-3-13_order_condition_accept_flex_rev.pdf.

FERC concluded that the ISO’s market rules require resources with a CSO to procure fuel to meet the terms of the resource’s energy market offer if fuel is physically available. FERC, Order on Complaint, New England Power Generators Association v. ISO New England (August 27, 2013), http://www.iso-ne.com/regulatory/ferc/orders/2013/aug/el13-66_8-27-13_order_nepga_complaint.pdf.

An Abnormal Conditions Alert is a notice from the ISO to applicable power system operations, maintenance, construction, and test personnel, as well as each applicable market participant, to alert them about an existing abnormal condition affecting the reliability of the power system or about an anticipated abnormal condition. Master/Local Control Center Procedure No. 2 (M/LCC2), Abnormal Conditions Alert (February 21, 2014), http://www.iso-ne.com/rules_proceds/operating/mast_satllte/mlcc2.pdf.

Hour ending denotes the preceding hourly period. For example, 12:01 a.m. to 1:00 a.m. is hour ending 1:00 a.m. Hour ending 5:00 p.m. is the period from 4:01 p.m. to 5:00 p.m.

The January 15, 2004, cold snap recorded the lowest average temperature in the last 20 years and the all-time winter peak of 22,818 MW.

The tariff, Section I, defines a limited-energy resource as a generating resource that, because of design considerations; environmental restriction on operations; cyclical requirements, such as the need to recharge or refill or manage water flow; or fuel limitations, is unable to operate continuously at full output on a daily basis. (See http://www.iso-ne.com/regulatory/tariff/sect_1/sect_i.pdf and Market Rule 1, http://www.iso-ne.com/regulatory/tariff/sect_3/index.html.) The ISO’s AMR12, Section 2.1.4, contains additional information on the LEG provisions; http://www.iso-ne.com/static-assets/documents/markets/mkt_anlys_rpts/annl_mkt_rpts/2012/amr12_final_051513.pdf.

NEPOOL Participants Committee February 2014 COO Report, NEPOOL Participants Committee presentation (February 1, 2014).

ICF International (ICF), Gas-Fired Power Generation in Eastern New York and its Impact on New England’s Gas Supplies, white paper (November 18, 2013), http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/mtrls/2013/nov202013/icf_upstream_gen_impacts_white_paper_11-18-2013.pdf.

ICF, Assessment of New England’s Natural Gas Pipeline Capacity to Satisfy Short and Near-Term Electric Generation Needs: Phase II (December 16, 2013), http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/mtrls/2013/dec182013/a3_draft_icf_phase_2_gas_study_report_without_appendices.pdf. See additional scenarios in the ICF PAC presentation, Winter 2013/14 Benchmark and Revised Projections for New England Natural Gas Supplies and Demand (April 29, 2014), http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/mtrls/2014/apr292014/a3_icf_benchmarking_study.pdf.

EIPC, “Gas-Electric System Interface Study,” webpage (2014), http://www.eipconline.com/Gas-Electric.html.

ICF (November 18, 2013).

ICF, Assessment of New England’s Natural Gas Pipeline Capacity to Satisfy Short and Near-Term Electric Generation Needs, draft report (June 15, 2012), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/reports/2012/gas_study_ceii.pdf. Also see the ISO’s memo to the PAC regarding this study (June 15, 2012), http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/reports/2012/gas_study_ltr.pdf.

Both the Phase I and Phase II studies considered the retirement of Vermont Yankee.

The analysis used 20 years of weather data and the results of analysis to derive relationships among mean daily temperatures and daily LDC demands, pipeline flows on the M&N system, and Distrigas sendout and other LNG operations during peak load periods. Gas supplies on the interstate pipelines (other than M&N pipeline) were assumed to equal the firmly contracted capacities.

More comprehensive discussions are available in the ISO’s 2014 Regional Electricity Outlook (February 25, 2014), http://www.iso-ne.com/aboutiso/fin/annl_reports/2000/2014_reo.pdf; 2014 Wholesale Markets Project Plan (May 9, 2014), http://www.iso-ne.com/static-assets/documents/pubs/whlsle_mkt_pln/2014_wmpp.pdf; and AMR13 (May 6, 2014), http://www.iso-ne.com/static-assets/documents/markets/mkt_anlys_rpts/annl_mkt_rpts/2013/2013_amr_final_050614.pdf.

ISO New England Inc. and NEPOOL, Energy Market Offer Flexibility Changes, FERC filing (July 1, 2013), http://www.iso-ne.com/regulatory/ferc/filings/2013/jul/er13-1877-000_mkt_offer_flex_7-1-2013.pdf.

The declaration of a Minimum Generation (Min Gen) Emergency is called when the on-line generation plus net imports comes close to exceeding system load and all generators are operating at economic minimum (ecomin) (i.e., the minimum amount of electricity output [in megawatts] available from a generating resource for economic dispatch). A Min Gen Emergency resets the economic minimums of resources down to their emergency minimums (if available) to gain additional dispatchable range, and it administratively sets LMPs to zero.

ISO New England Inc. and New England Power Pool Participants Committee, Docket No. ER14-1639-___, Compliance Filing Providing Additional Explanation Concerning the Limited Exemption from Offer Review Trigger Price Review for Renewable Technology Resources (July 11, 2014), http://www.iso-ne.com/static-assets/documents/regulatory/ferc/filings/2014/jul/er14_1639_001_7_11_14_compliance_renewables_exempt.pdf.

FERC, Communication of Operational Information between Natural Gas Pipelines and Electric Transmission Operators, Order No. 787, final rule (November 15, 2013), http://www.ferc.gov/CalendarFiles/20131115164637-RM13-17-000.pdf.

ISO New England, Pipeline Information-Sharing Changes, FERC filing (January 10, 2014), http://www.iso-ne.com/regulatory/ferc/filings/2014/jan/er14-970-000_1-10-2014_pipe_inf_sharing.pdf.

ISO New England Inc., Docket No. ER14-___-000, Winter 2014-15 Reliability Program (Parts 1 and 2), FERC filing (July 11, 2014), http://www.iso-ne.com/static-assets/documents/regulatory/ferc/filings/2014/jul/er14_2407_000_win_rel_pro_7_11_2014.pdf and http://www.iso-ne.com/regulatory/ferc/filings/2014/jul/er14-2407-001_winter_rel_7-11-2014.pdf. Also see “ISO-NE and NEPOOL File Proposal with FERC to Implement a Winter Reliability Program for Winter 2014/2015” (ISO Newswire, July 14, 2014), http://isonewswire.com/updates/2014/7/14/iso-ne-and-nepool-file-proposal-with-ferc-to-implement-a-win.html. FERC, Order Accepting Tariff Revisions, (September 9, 2014), http://www.iso-ne.com/static-assets/documents/2014/09/er14-2407-000_9-9-14_order_accept_winter_reliability.pdf.

“New England Governors’ Commitment to Regional Cooperation on Energy Infrastructure Issues,” (n.d.), http://www.nescoe.com/uploads/New_England_Governors_Statement-Energy_12-5-13_final.pdf.

FERC, Coordination of the Scheduling Processes of Interstate Natural Gas Pipelines and Public Utilities, 146 FERC ¶ 61,201, notice of proposed rulemaking (March 20, 2014), http://elibrary.ferc.gov/idmws/Doc_Family.asp?document_id=14196317.

FERC, Order Initiating Investigation into ISO and RTO Scheduling Practices and Establishing Paper Hearing Procedures (March 20, 2014), http://www.ferc.gov/whats-new/comm-meet/2014/032014/M-2.pdf.

Under an emissions trading program, an emissions allowance is the authorization for a source of a pollutant to emit one ton of the pollutant (e.g., SO2, nitrogen oxides [NOX,] or carbon dioxide [CO2]) during a specific compliance period.

RGGI is a mandatory, market-based effort to reduce greenhouse gas emissions in the Northeast and Mid-Atlantic states through a multistate CO2 emissions budget cap-and-trade program.

EPA, National Pollutant Discharge Elimination System—Final Regulations to Establish Requirements for Cooling Water Intake Structures at Existing Facilities and Amend Requirements at Phase I Facilities, final rulemaking, 79 FR 48299 (August 15, 2014); applies to existing and new cooling water intake structures at power plants and manufacturers. EPA, Effluent Limitation Guidelines and Standards for the Stream Electric Power Generating Point Source Category, proposed rule, 78 FR 34431 (June 7, 2013). The main pollutants of concern for these discharges include metals (mercury, arsenic, and selenium), nitrogen, and total dissolved solids generated by the operation of air pollution control devices (i.e., scrubbers).

The requirement for reducing impingement mortality recognizes seven compliance alternatives that regulators may require: (1) operate a closed-cycle recirculating system; (2) operate a cooling water intake structure with a maximum through-screen design intake velocity of 0.5 feet per second (fps); (3) operate a cooling water intake structure with a maximum through-screen intake velocity of 0.5 fps; (4) operate an offshore velocity cap installed before the effective date of this rule; (5) operate a modified traveling screen that regulators determine is the best technology available for impingement reduction; (6) operate any other combination of technologies, management practices, and operational measures that regulators determine is the best technology available for impingement reduction; or (7) achieve the specified impingement mortality performance standard. EPA, NPDES— Final Cooling Water Intake Structures Regulations, 48299, see above footnote.

Endangered Species Act of 1973, as amended through the 108th Congress, http://www.fws.gov/endangered/esa-library/pdf/ESAall.pdf.

EPA, Effluent Limitations Guidelines and Standards for the Steam Electric Power Generating Point Source Category, proposed rule, 78 FR 34432 (June 7, 2013). EPA proposes revisions to existing (circa 1982) wastewater effluent limitation guidelines for power plants to address the changing toxicity of power plant wastewater discharge streams from scrubbers and other air pollution control systems required by air quality regulations.

EPA, National Ambient Air Quality Standards for Ozone, final rule, 73 FR 16436 (March 27, 2008); National Ambient Air Quality Standards for Particulate Matter, final rule, 78 FR 3086 (January 15, 2013); National Ambient Air Quality Standards for Sulfur Dioxide, final rule, 75 FR 35520 (June 22, 2010).

EPA, National Emission Standards for Hazardous Air Pollutants: Coal- and Oil-fired Electric Utility Steam Generating Units, final rule 77 FR 9304 (February 16, 2012). EPA developed standards under Section 112(d) to reduce hazardous air pollutant emissions from this source category. MATS was proposed on May 3, 2011 (76 FR 24976) and included proposed amendments to the criteria pollutant NSPS for utilities.

The “good neighbor” requirements address air pollution transported from an upwind state to a downwind state.

EPA, Finding of Significant Contribution and Rulemaking for Certain States in the Ozone Transport Assessment Group Region for Purposes of Reducing Regional Transport of Ozone (NOX SIP Call), final rule, 63 FR 57356 (October tr527, 1998), https://federalregister.gov/a/98-26773. EPA, Revisions to the NOX SIP Call, final rule, 70 FR 25162 (May 12, 2005). EPA, Rule to Reduce Interstate Transport of Fine Particulate Matter and Ozone (Clean Air Interstate Rule). EPA, Federal Implementation Plans: Interstate Transport of Fine Particulate Matter and Ozone and Correction of SIP Approvals, final rule, 76 FR 48207 (August 8, 2011), https://federalregister.gov/a/2011-17600.

Clean Air Act Title IV—Acid Deposition Control, §§ 401-416, 42 USC §§ 7651-7651o; EPA CAIR (see above note); Revisions to Acid Rain Program; Revisions to the NOX SIP Call, final rule, 70 FR 25162 (May 12, 2005).

EIA, Annual Energy Outlook 2013, “Issues in Focus—4. Competition between coal and natural gas in the electric power sector” (April 15, 2013), http://www.eia.gov/forecasts/aeo/IF_all.cfm#coal_gas.

The states joining the EPA petition are Connecticut, Delaware, Maryland, Massachusetts, New Hampshire, New York, Rhode Island, and Vermont. (Maine, Washington DC, and several Northern Virginia counties are also in the OTR.) The nine states they are asking EPA to add to the OTR are Illinois, Indiana, Kentucky, Ohio, Michigan, North Carolina, Tennessee, Virginia, and West Virginia.

2012 ISO New England Electric Generator Air Emissions Report (January 2014), http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/eag/mtrls/2014/mar52014/2012_emissions_report.pdf.

RGGI, Inc., “Program Overview,” webpage (n.d.), http://www.rggi.org/design/overview. The RGGI CO2 budget (cap) is equal to the total number of CO2 allowances issued by RGGI states in a given year. A CO2 allowance represents a limited authorization to emit one short ton of CO2 from a regulated source, as issued by a participating state. During the current control period (2012–2014), the cap is 165 million short tons of CO2/yr for the nine-state region.

RGGI, Inc., “Updated Model Rule,” on 2012 Program Review webpage (February 7, 2013), http://www.rggi.org/design/program-review.

EPA, Standards of Performance for Greenhouse Gas Emissions from New Stationary Sources: Electric Utility Generating Units, proposed rule, 79 FR 1429 (January 8, 2014), https://www.federalregister.gov/articles/2014/01/08/2013-28668/standards-of-performance-for-greenhouse-gas-emissions-from-new-stationary-sources-electric-utility. EPA proposed separate performance standards for fossil steam generating units and stationary combustion turbines.

EPA, Standards of Performance for Greenhouse Gas Emissions for New Stationary Sources: Electric Utility Generating Units, proposed rule, 77 FR 22392 (April 13, 2012). Affected units would have included electric utility steam generating units (boilers); stationary combined-cycle combustion turbines and their associated heat-recovery steam generators (HRSGs) and duct burners; and integrated combined-cycle (IGCC) units, including their combustion turbines and associated HRSGs. EPA, Withdrawal of Proposed Standards of Performance for Greenhouse Gas Emissions From New Stationary Sources: Electric Utility Generating Units, 79 FR 1352 (January 8, 2014).

EIA, Annual Energy Outlook 2014 Reference Case, Power Sector CO2 Emissions Sensitive to Policy Changes and Natural Gas Supply (June 9, 2014), http://www.eia.gov/todayinenergy/detail.cfm?id=16611. Executive Office of the President, “Power Sector Carbon Pollution Standards,” 78 FR 39533 (July 1, 2013), https://federalregister.gov/a/2013-15941.

EPA, GHG New Source Performance Standard, 77 FR 22392, 22398 (April 13, 2012), http://www.federalregister.gov/a/2012-7820/p-219. EPA excluded simple-cycle turbines because they generally are used much less often (and thus have lower GHG emissions) and mostly to meet peak demand rather than baseload or intermediate load requirements.

EPA, Carbon Pollution Emission Guidelines for Existing Stationary Sources: Electric Utility Generating Units, proposed rule, 79 FR 34829 (June 18, 2014), https://federalregister.gov/a/2014-13726, and Carbon Pollution Standards for Modified and Reconstructed Stationary Sources: Electric Utility Generating Units, proposed rule,
79 FR 34959 (June 18, 2014), https://federalregister.gov/a/2014-13725.

“ISO New England Issues Statement on Entergy’s Announcement to Retire Vermont Yankee Nuclear Plant,” press release (August 27, 2013), http://www.iso-ne.com/nwsiss/pr/2013/iso_new_england_issues_statement_vy_retirement_final.pdf. The ISO studied the needs of the high-voltage power system serving Vermont and New Hampshire and concluded system reliability will be maintained.

New York v. NRC, 681 F.3d 471 (D.C. Cir. 2012). The court found that NRC violated the National Environmental Policy Act by failing to consider potential environmental effects in the event a permanent repository for disposing of spent nuclear fuel is never built. The court also found that the NRC’s consideration of leaks and fires involving spent fuel pools at nuclear power plants was deficient. Nuclear Regulatory Commission, Consideration of Environmental Impacts of Temporary Storage of Spent Fuel after Cessation of Reactor Operation, final rule, 75 Fed. Reg. 81032 (December 23, 2010), and NRC, Waste Confidence Decision Update, 75 Fed. Reg. 81037 (December 23, 2010).

Environmental Protection Agency, Environmental Radiation Protection Standards for Nuclear Power Operations, advance notice of proposed rulemaking, 79 FR 6509 (February 4, 2014).

FERC, Hydropower Licensing webpage (June 10, 2013), http://www.ferc.gov/industries/hydropower/gen-info/licensing.asp.

FERC, Modification to Integrated Licensing Process Schedule, Transcanada Hydro Northeast, Inc., and Firstlight Hydro Generating Company (December 21, 2012); Connecticut River Joint Commission, Relicensing of Connecticut River Dams (Accessed February 18, 2014).

Hydropower Regulatory Efficiency Act of 2013, Pub. L 113-23 (August 9, 2013). The act also directs DOE to study the operational flexibility that existing pumped-storage facilities offer in support of intermittent renewable electric energy generation, including the potential for such facilities to be upgraded or retrofitted with advanced, commercially available technology and the potential of existing pumped-storage facilities and new advanced pumped-storage facilities to provide grid-reliability benefits.

NREL, The Western Wind and Solar Integration Study Phase 2, NREL/TP-5500-55588, technical report (DOE, September 2013), http://www1.eere.energy.gov/wind/pdfs/55588.pdf.

Note that the Aroostook, ME, region is considered to need major transmission line construction. ISO New England, Northern Maine System Performance, PAC presentation (September 21, 2010), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2010/sep212010/northern_maine.pdf.

TCSCs are series capacitors that can change their impedance within a fraction of a cycle. They are a type of flexible alternating-current transmission system (FACTS) device that uses a thyristor—a power electronics component that provides the ability to switch output. (See Section 7.4.2.3 for more on FACTS devices.)

On December 27, 2012, the DOE Solar Program awarded funding to the IBM Thomas J. Watson Research Center (DOE Award No. DE-EE0006017). More information is available at http://solarhighpen.energy.gov/project/ibm_thomas_j_watson_research_center_watt_sun_multi_scale_multi_model_machine_learning_solar.

Artificial neural networks are computational models capable of machine learning and pattern recognition.

PV Forecast in Transmission Planning Studies, PAC presentation (July 11, 2014), http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/mtrls/2014/jul112014/a_use_of_pv_in_long_term_transmission_planning.pdf.

IEEE 1547 establishes criteria and requirements for the interconnection of distributed resources with electric power systems. This document provides a uniform standard for the performance, operation, testing, safety considerations, and maintenance of the interconnection. See “IEEE 1547 Standard for Interconnecting Distributed Resources with Electric Power Systems,” webpage (2014), http://grouper.ieee.org/groups/scc21/1547/1547_index.html.

IEEE 1547 and interconnection requirements for low/high- voltage ride through, low/high-frequency ride through, ramp rates, and others.

ISO New England, 2012 Economic Study, final report (April 30, 2014), http://www.iso-ne.com/static-assets/documents/committees/comm_wkgrps/prtcpnts_comm/pac/reports/2014/a9_2012_economic_study_final.pdf, and 2011 Economic Study, final report  (March 31, 2014), http://www.iso-ne.com/static-assets/documents/committees/comm_wkgrps/prtcpnts_comm/pac/reports/2014/2011_eco_study_final.pdf.

Both studies modeled 8,760 hours of both onshore and offshore wind outputs based on the results of the ISO’s New England Wind Integration Study (NEWIS), final report (December 5, 2010), http://www.iso-ne.com/static-assets/documents/committees/comm_wkgrps/prtcpnts_comm/pac/reports/2010/newis_report.pdf.

Preliminary Results for 2012 Economic Study Request Specific Scenario Phase and IREMM 2012 Economic Study Update, PAC presentations (January 17, 2013), http://www.iso-ne.com/static-assets/documents/committees/comm_wkgrps/prtcpnts_comm/pac/mtrls/2013/jan172013/eco_study_results.pdf and http://www.iso-ne.com/static-assets/documents/committees/comm_wkgrps/prtcpnts_comm/pac/mtrls/2013/jan172013/a2_iremm_2012_economic_study_update_011713.pdf. The simulation was run using IREMM, which uses a simplified pipe and bubble representation of the of the transmission system that reflects first-contingency limits but does not capture all reliability requirements. The study reflected resource retirements and additions effective as of FCA #5.

NYISO and PJM redispatch resources to permit a loss-of-source of at least 1,200 MW. A higher limit is permissible when favorable system conditions exist in both NYISO and PJM. This limit typically has been no lower than 1,400 MW in recent years.

ISO New England, Update on Generic Supply-Side Resource Capital Costs, PAC presentation (April 29, 2014), http://www.iso-ne.com/static-assets/documents/committees/comm_wkgrps/prtcpnts_comm/pac/mtrls/2014/apr292014/a8_generic_capital_costs_of_supply_side_resources_rev2.pdf.

US EIA, "Updated Capital Cost Estimates for Utility Scale Electricity Generating Plants," (DOE, 2013), http://www.eia.gov/forecasts/capitalcost/pdf/updated_capcost.pdf, and EPRI, Program on Technology Innovation: Integrated Generation Technology Options 2012, ( 2013), http://www.epri.com/abstracts/Pages/ProductAbstract.aspx?productId=000000000001026656. The Brattle Group’s, “Stakeholder Demand Curves: Performance Summary Table (Net CONE - $11.08)” (March 11, 2014) shows the capital cost assumptions developed for the ISO. See http://www.iso-ne.com/static-assets/documents/committees/comm_wkgrps/mrkts_comm/mrkts/mtrls/2014/mar12132014/a02a_the_brattle_group_stakeholder_demand_curves_performance_summary_03_11_14.pptx.

RSP13, Section 6.9 (November 8, 2013), http://www.iso-ne.com/trans/rsp/index.html.

A repowered generator may require transmission system improvements to qualify for the FCM, as identified by an FCA overlapping interconnection impact analysis, which the ISO conducts for each new supply-side resource to assess whether the resource can provide useful capacity and electric energy without negatively affecting the ability of other capacity resources to provide these services also.

Nontransmission Alternatives Analysis: Results of the NH/VT Pilot Study, PAC presentation (May 26, 2011), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2011/may262011/nta_analysis.pdf.

Market Resource Alternative Analysis—Final Supply-Side Results Greater Hartford and Central Connecticut, PAC presentation (December 13, 2012), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2012/dec132012/ghcc_mra.pdf, and Market Resource Alternative Analysis—Demand-Side Results Greater Hartford and Central Connecticut, revised, PAC presentation (November 14, 2012), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2012/nov142012/ghcc_mra_november.pdf.

Market Resource Alternative Analysis—Southeast Massachusetts/Rhode Island, PAC presentation (April 29, 2014), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2014/apr292014/a6_sema_ri_market_resource_alternatives.pdf.

More information about NERC is available at http://www.nerc.com/.

Additional information on the EIPC is available at http://www.eipconline.com/.

EIPC, Steady State Modeling and Load Flow Working Group Report for 2018 and 2023 Roll-Up Integration Cases, Final Report (February 14, 2014), http://www.eipconline.com/uploads/FINAL_EIPC_Roll-up_Report_Feb14-2014.pdf.

Scenario information is available at the EIPCC webpage, “Non-DOE Documents:” http://www.eipconline.com/Non-DOE_Documents.html. Information on stakeholder activities is available at http://www.eipconline.com/Stakeholder_Activities.html.

See NERC’s “Reliability Assessment and Performance Analysis,” webpage (2013), http://www.nerc.com/pa/RAPA/Pages/default.aspx.

NERC, 2013 Long-Term Reliability Assessment (December 2013), http://www.nerc.com/pa/RAPA/ra/Reliability%20Assessments%20DL/2013_LTRA_FINAL.pdf.

ReliabilityFirst Corporation preserves and enhances the reliability of the bulk power system across 13 states and the District of Columbia by setting and enforcing electric reliability standards. Additional information about RFC is available at https://www.rfirst.org/Pages/Rfirst.aspx.

IRC, “Reports and Filings,” webpage (2014), http://www.isorto.org/Reports/default.

The NPCC region covers nearly 1.2 million square miles populated by more than 55 million people. NPCC in the United States includes the six New England states and the state of New York. NPCC Canada includes the provinces of Ontario, Québec, and the Maritime provinces of New Brunswick and Nova Scotia. As full members, New Brunswick and Nova Scotia also ensure that NPCC reliability issues are addressed for Prince Edward Island.

Northeastern ISO/RTO Planning Coordination Protocol (2004), http://www.iso-ne.com/static-assets/documents/committees/comm_wkgrps/othr/ipsac/rto_plan_prot/planning_protocol.pdf.

All IPSAC materials are available at http://www.iso-ne.com/committees/planning/ipsac.

ISO New England, New York ISO, and PJM, 2013 Northeast Coordinated System Plan (April 16, 2014), http://www.iso-ne.com/static-assets/documents/committees/comm_wkgrps/othr/ipsac/mtrls/2014/mar282014/2013_ncsp.pdf.

Net imports over external ties = [{(18,961 GWh) ÷ (129,377 GWh net energy for load + 1,624 GWh pumping load)} × 100] = 14.47%.

Energy Policy Act of 2005, Pub. L. 109-58, Title XII, Subtitle B, 119 Stat. 594 (2005) (amending the Federal Power Act to add a new § 216).

FERC, Transmission Planning and Cost Allocation by Transmission Owning and Operating Public Utilities, Order No. 1000, 18 CFR Part 35, 136 FERC ¶ 61,051 (July 21, 2011), http://www.ferc.gov/industries/electric/indus-act/trans-plan.asp and http://www.ferc.gov/whats-new/comm-meet/2011/072111/E-6.pdf. Preventing Undue Discrimination and Preference in Transmission Service, 18 CFR Parts 35 and 37, Order No. 890 (February 16, 2007), http://www.ferc.gov/whats-new/comm-meet/2007/021507/E-1.pdf.

ISO New England, Order No. 1000 Compliance Filing of ISO New England Inc. and the Participating Transmission Owners Administrative Committee, Part 1 of 2 (October 25, 2012), http://www.iso-ne.com/regulatory/ferc/filings/2012/oct/er13-193-000_10-25-12_order_1000_compliance_part_1.pdf. Also, Order No. 1000 Interregional Compliance Filing of ISO New England Inc. and the Participating Transmission Owners Administrative Committee, Supported by the New England Power Pool Participants Committee (July 10, 2013). http://www.iso-ne.com/static-assets/documents/regulatory/ferc/filings/2013/jul/er13_1960_000_7_10_2013_order_1000.pdf.

FERC, Order on Compliance Filings (May 17, 2013), http://www.iso-ne.com/regulatory/ferc/orders/2013/may/er13-193_er13-196_5-17_13_order_on_order_1000_compliance_filings.pdf.

ISO New England, Request for Rehearing on Order No. 1000 Compliance Order (June 17, 2013), http://www.iso-ne.com/regulatory/ferc/filings/2013/jun/er13-193_er13-196_6-17-13request_rehear_ordr1000.pdf.

National Interest Electric Transmission Corridors and Congestion Study documents are available at http://energy.gov/oe/services/electricity-policy-coordination-and-implementation/transmission-planning/national-2.

DOE, Draft National Electric Transmission Congestion Study (August 2014), http://www.energy.gov/oe/articles/draft-national-electric-transmission-congestion-study-now-available-public-comment.

Piedmont Environmental Council v. FERC, 558 F.3d 304 (4th Cir. 2009).

DOE, Transmission Constraints and Congestion in the Western and Eastern Interconnections, 2009–2012 (January 2014), http://energy.gov/oe/downloads/transmission-constraints-and-congestion-western-and-eastern-interconnections-2009-2012.

NIST, Framework for Improving Critical Infrastructure Cybersecurity (February 12, 2014), http://www.nist.gov/cyberframework/upload/cybersecurity-framework-021214-final.pdf.

FERC, Order Directing Filing of Standards (March 7, 2014), http://www.ferc.gov/CalendarFiles/20140307185442-RD14-6-000.pdf.

For more information about NESCOE, see www.nescoe.com.

NESCOE, New England Natural Gas Infrastructure and Electric Generation: Constraints and Solutions (April 16, 2013), http://www.nescoe.com/Gas_Supply_Study.html.

NESCOE, Natural Gas Infrastructure and Electric Generation: Proposed Solutions for New England (August 26, 2013), http://nescoe.com/Gas_Supply_Study.html.

NESCOE, “Request for ISO-NE technical support and assistance with tariff filings related to electric and natural gas infrastructure in New England,” memo (January 21, 2014), http://www.nescoe.com/uploads/RequestISO-NEassistanceTransGas_21Jan2014.pdf.

Gordon Van Welie, “NESCOE’s Request for ISO-NE Technical Support and Assistance with Tariff Filings Related to Electric and Natural Gas Infrastructure in New England,” letter to NESCOE (January 28, 2014), http://www.iso-ne.com/pubs/pubcomm/corr/2014/2014_01_28_response_to_nescoe.pdf.

ISO New England, “Presentations, Speeches, and Other Materials,” webpage, “External Affairs Monthly Issues Memo” document type, http://www.iso-ne.com/about/government-industry-affairs/materials.

Eric Runge, “Sector Caucus Representatives for the EIPC,” memorandum (June 23, 2010), http://www.iso-ne.com/committees/comm_wkgrps/othr/eipc/eipc_caucus_reps.doc.

Additional information on the CLG is available at http://www.iso-ne.com/committees/consumer-liaison.

ISO New England and Consumer Liaison Group Coordinating Committee, 2014 Report of the Consumer Liaison Group (May 28, 2014), http://www.iso-ne.com/static-assets/documents/committees/comm_wkgrps/othr/clg/annual_rpts/2013_clg_report_final.pdf.

See the ISO’s Wholesale Markets Project Plans at http://www.iso-ne.com/markets-operations/markets-development/wholesale-markets-project-plan.

The Institute of Electrical and Electronics Engineers (IEEE) describes the smart grid as a “next-generation” electrical power system that typically employs the increased use of communications and information technology for generating, delivering, and consuming electrical energy. See the IEEE’s Smart Grid Community for a full discussion of smart grid technology that is available at https://www.ieee.org/membership-catalog/productdetail/showProductDetailPage.html?product=CMYSG735.

PMUs use global positioning satellite technology to monitor the performance of the region’s electric power grid accurately and provide specific data, including synchrophasor power system measurements, for use in operating the grid and enhancing grid design. The IEEE defines FACTS as flexible alternating-current transmission systems that incorporate power-electronics-based controllers and other static controllers to enhance controllability and power-transfer capability. See http://www.ieee-pes.org/nari-hingorani-facts-award.

For additional information on PSERC and EPRI, refer to http://www.pserc.wisc.edu/home/index.aspx and http://www.epri.com/.

EIA, ”Electric Power Sales, Revenue, and Energy Efficiency Form EIA-861, detailed data files,” webpage (December 9, 2013) http://www.eia.gov/electricity/data/eia861/.

Additional information on NIST is available at http://www.nist.gov/index.html. Also see NIST’s “Smart Grid Interoperability Panel” webpage, http://www.nist.gov/smartgrid/sgipbuffer.cfm.

ISO/RTO Council, “2013 North American Demand-Response Characteristics Available” (February 28, 2014), http://www.isorto.org/Reports/default.

For more information on IEEE, see http://www.ieee.org/index.html.

Allison Silverstein, NASPI and Synchrophasor Technology Milestones—We’re Making Progress!, slide deck (North American SynchroPhasor Initiative, October 22, 2013), slide 2 (map illustrating all the PMUs installed in North America as of October 2013), http://www.naspi.org/file.aspx?fileid=1150.

Michael Henderson and Donald Ramey, Planning Issues for FACTS, presentation at the IEEE Power Engineering Society General Meeting, Tampa (June 2007). Also see “Transmission System Application Requirements for FACTS Controllers Special Publication 06TP178,” produced by the IEEE Power Engineering Society Working Group 15.05.13. Also see M. Henderson and D. Ramey, “Planning Issues for FACTS,” IEEE PES T&D Conference and Exhibition presentation (New Orleans, April 2010), http://ieeexplore.ieee.org/xpl/articleDetails.jsp?arnumber=5484247&searchWithin%3DFACTS%26sortType%3Dasc_p_Sequence%26filter%3DAND%28p_IS_Number%3A5484192%29.

See RSP13, Section 5.4, http://www.iso-ne.com/static-assets/documents/trans/rsp/2013/rsp13_final.docx.

Static VAR compensators and DVARs provide dynamic voltage support.

OATT, Attachment K, http://www.iso-ne.com/regulatory/tariff/sect_2/oatt/sect_ii.pdf. Transmission Planning Process Guide, draft, http://www.iso-ne.com/static-assets/documents/committees/comm_wkgrps/prtcpnts_comm/pac/plan_guides/plan_process_guide/planning_process_guide_for_february_pac_2_5_2013__3_.docx, and Transmission Planning Technical Guide, draft, http://www.iso-ne.com/static-assets/documents/committees/comm_wkgrps/prtcpnts_comm/pac/plan_guides/plan_tech_guide/planning_technical_guide_clean_12_06_2013.pdf.

In June 2013, Southern Connecticut Gas, Connecticut Natural Gas, and Yankee Gas submitted a joint expansion plan to DEEP and the Public Utilities Regulatory Authority (PURA) to provide gas heating service to approximately 280,000 additional residents and businesses in Connecticut over the next 10 years. PURA approved the plan on November 22, 2013. CT Public Act No. 13-298, An Act Concerning Implementation of Connecticut’s Comprehensive Energy Strategy and Various Revisions to the Energy Statutes required the expansion plan.

State of Connecticut, An Act Concerning Connecticut’s Clean Energy Goals, Public Act No. 13-303, http://www.cga.ct.gov/2013/ACT/PA/2013PA-00303-R00SB-01138-PA.htm.

The CT PURA webpage, “Connecticut Renewable Portfolio Standards Overview” (2014) (http://www.ct.gov/pura/cwp/view.asp?a=3354&q=415186) provides a fully up-to-date definition of Class I renewable energy sources.

Renewable Energy Certificates are tradable, nontangible commodities, each representing the eligible renewable generation attributes of 1 MWh of actual generation from a grid-connected renewable resource.

DEEP selected two projects that PURA later approved: (1) Number Nine Wind Farm, a proposed 250 MW land-based wind project located in Aroostook County, Maine, for a contract term of 15 years; and (2) Fusion Solar Center, a proposed 20 MW PV system located in Sprague and Lisbon, Connecticut, for a contract term of 20 years.

The state enacted legislation in 2011 (Public Act 11-80) directing the Connecticut Siting Council to develop wind-siting regulations and barring it from acting on any siting applications or petitions until after the adoption of these regulations.

MPUC, Report to the Legislature Pursuant to Resolves 2013, Chapter 45, Regarding Geomagnetic Disturbances and Electromagnetic Pulse, (January 20, 2014).

Maine PUC, Maine Public Utilities Commission Review of Natural Gas Capacity Options (February 26, 2014), http://www.maine.gov/tools/whatsnew/attach.php?id=615609&an=1.

State of Maine, An Act to Support Solar Energy Development in Maine, Pub. L. 2013, Chapter 562 (April 24, 2014), http://www.mainelegislature.org/legis/bills/getPDF.asp?paper=SP0644&item=3&snum=126.

MA DPU, Investigation by the Department of Public Utilities upon Its Own Motion into Time Varying Rates, DPU 14-04-B (June 12, 2014), http://www.mass.gov/eea/docs/dpu/orders/d-p-u-14-04-b-order-6-12-14.pdf.

MA DPU, Investigation by the Department of Public Utilities on its own Motion into Modernization of the Electric Grid, DPU 12-76-B (June 12, 2014), http://www.mass.gov/eea/docs/dpu/orders/dpu-12-76-b-order-6-12-2014.pdf.

Commonwealth of Massachusetts, An Act Relative to Credit for Thermal Energy Generated with Renewable Fuels, H. 4385 (July 31, 2014), https://malegislature.gov/Bills/188/House/H4385.

PSNH, Report on Investigation into Market Conditions, Default Service Rate, Generation Ownership, and Impacts on the Competitive Electricity Market, IR 13-020 (June 7, 2013), http://www.puc.nh.gov/Electric/IR%2013-020%20PSNH%20Report%20-%20Final.pdf.

PSNH, Preliminary Status Report Addressing the Economic Interest of PSNH’s Retail Customers as it Relates to the Potential Divestiture of PSNH’s Generating Plants, IR 13-020 (April 1, 2014), http://www.puc.state.nh.us/Regulatory/Docketbk/2013/13-020/LETTERS-MEMOS-TARIFFS/13-020%202014-04-01%20STAFF%20PRELIMINARY%20STATUS%20RPT_PSNH%20GENERATING%20PLANTS.PDF.

PSNH, Preliminary Status Report Addressing the Economic Interest of PSNH’s Retail Customers as it Relates to the Potential Divestiture of PSNH’s Generating Plants, p. 10, IR 13-020 (April 1, 2014), http://www.puc.state.nh.us/Regulatory/Docketbk/2013/13-020/LETTERS-MEMOS-TARIFFS/13-020%202014-04-01%20STAFF%20PRELIMINARY%20STATUS%20RPT_PSNH%20GENERATING%20PLANTS.PDF.

State of New Hampshire, An Act Relative to the Divestiture of PSNH Assets, HB1602 (June 4, 2014), http://www.gencourt.state.nh.us/legislation/2014/HB1602.pdf.

State of New Hampshire, An Act Establishing a State Energy Strategy, SB 191 (July 24, 2013), http://legiscan.com/NH/text/SB191/id/792744.

OEP, New Hampshire’s Energy Facility Siting Process: Report on Stakeholder and Citizen Feedback (December 31, 2013), http://www.nh.gov/oep/energy/programs/documents/sb99reportonstakeholderandcitizenfeedback.pdf.

State of New Hampshire, An Act Relative to the Siting of Energy Facilities, SB245 (June 4, 2014), http://www.gencourt.state.nh.us/legislation/2014/SB0245.pdf. State of New Hampshire, An Act Relative to the Divestiture of PSNH Assets, HB1602 (June 4, 2014), http://www.gencourt.state.nh.us/legislation/2014/HB1602.pdf.

State of New Hampshire, An Act Requiring the Development of an Energy-Efficiency Implementation Plan, HB 1129 (June 4, 2014), http://www.gencourt.state.nh.us/legislation/2014/HB1129.pdf.

In accordance with RI Gen. Laws § 39-26-6(d), the Rhode Island PUC reviewed the state’s RES to determine the adequacy, or potential adequacy, of renewable energy supplies to meet the increase in the percentage of energy required from these supplies to go into effect in 2015.

RI PUC, Order No. 21353, Docket No. 4404, Commission’s Review into the Adequacy of Renewable Energy Supplies pursuant to R.I. Gen. Laws § 39-26-6(d), (February 10, 2014).

State of Rhode Island, The Renewable Energy Growth Program, S 2690 Substitute A, as amended, and H 7727 Substitute A, as amended (June 2014), http://webserver.rilin.state.ri.us/BillText/BillText14/SenateText14/S2690Aaa.pdf and http://webserver.rilin.state.ri.us/BillText/BillText14/HouseText14/H7727Aaa.pdf.

State of Rhode Island, Affordable Clean Energy Security Act, S 2439 Substitute A, as amended, and H 7991 Substitute A (June 2014), http://webserver.rilin.state.ri.us/BillText/BillText14/SenateText14/S2439Aaa.pdf and http://webserver.rilin.state.ri.us/BillText/BillText14/HouseText14/H7991A.pdf.

State of Rhode Island, Resilient Rhode Island Act, H 7904 Substitute A (July 2014), http://webserver.rilin.state.ri.us/PublicLaws/law14/law14392.htm.

State of Vermont, An Act Relating to Self-Generation and Net Metering, H.702 (April 2, 2014), http://www.leg.state.vt.us/docs/2014/bills/Passed/H-702.pdf.